## Export
Order | Scheduled start | Functional Location | Description | Order Type | Technical obj. type | Priority text | G2 | E-Feedback | Description of functional location | PM/CM | Plant section | Notification | Equipment | Manufacturer | Discipline | Total actual costs | Actual work | Work | Cause Code Text | Cause Text | Object Part Text | Activity Text | Description
90230343 | 2016-01-25 | A081-0S0163B | 0S-0163B FLARE LINE 1ST ISOLATION VALVE | MX04 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10123061 | 700002200043 | DKME | Integrity | 25046.22 | 36 | 62 |  | - | Other - please specify in text field
90274086 | 2020-11-01 | A081-1F5111 | HW-VALVE TO BE PROVID AT TRNSFERLINE LPD | MX04 | M_FUR_X | Routine Wrk LvL 5 | 0 |  | SMR FURNACE | CM | LPU | 10146847 | 700002348459 | KTI | Integrity | 0 | 0 | 116 |  |  |  |  | 16.09.2014 06:42:16 Vijaykumar Bhailalbhai Patel (QRVPA5) VALVE TO BE PROVIDED AT 1F5111 PROCESS TRANFERLINE LPD. NOTE: SCAFFOLDING REQUIRED FOR APPROACH. 16.09.2014 08:51:48 Vijay Paramasivam (QRVPA3) Phone 44032412 Valve to be procured to install as per PEFS.
90275051 | 2017-05-07 | A081-0X0104 | 0X-0104 DRM CONVEYOR BELLOW DAMAGED-> | MX04 | M_PAC_CON2 | Routine Wrk LvL 5 | 0 |  | SCREW CONVEYOR | CM | FGP | 10147542 | 700002206193 |  | Electrical | 196.35 | 15 | 19 | Normal Wear | Normal Wear-Normal Wear | Other - please specify in text field | Replace
90279703 | 2016-04-29 | A081-0S0123A | 0S-0123A O/L LINE 1ST DRAIN VALVE TO DSG | MX04 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10149454 | 700002201322 | DKME | Integrity | 0 | 0 | 32
90314505 | 2017-04-22 | A081-2A8324 | OVERHAULING OF SPARE ROLLER ASSEMBLY | MX20 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP |  | 700002297332 |  | Integrity | 3.75 | 1 | 30
90329302 | 2016-05-01 | A081-0S0123A | HYDROCARBON FILTERS PERMANENT SCAFFOLD | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10173740 | 700002201322 | DKME | Integrity | 4552.2 | 0 | 48
90332715 | 2016-05-01 | A081-1S0241 | U-200 PH-1 FILTERS PERMANENT SCAFFOLD | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10175233 | 700002354895 | JFC CORPORATION | Integrity | 1438.73 | 0 | 81
90333249 | 2017-04-27 | A081-0S0123A | VALVE VENT PLUG REPLACEMENT, 0S-0123A->- | MX04 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10175574 | 700002201322 | DKME | Integrity | 6475.04 | 106 | 95 | Other - please specify in text field | Other - please specify in text field-due to aiging of plug oring | Other - please specify in text field | Replace
90333503 | 2017-01-21 | A081-1A8324 | Overhaul the spare roller assembly | MX20 |  | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP |  |  |  |  | 1829.31 | 62 | 89
90346159 | 2016-01-02 | A081-0S0143B | 0S-0143B Gearbox repair & requisition | MX04 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10181058 | 700002202402 | DKME | Integrity | 9236.66 | 189 | 153 | Normal Wear | Normal Wear-Normal Wear | Other - please specify in text field | Fix / Repair
90346707 | 2016-01-07 | A081-1F5111 | 1F-5111 MAIN AIR DAMPER E&F ROW STRUCK | MX04 | M_FUR_X | Routine Wrk Lvl 2 | 0 |  | SMR FURNACE | CM | LPU | 10181474 | 700002348459 | KTI | Integrity | 469.4 | 16 | 37 | Other - please specify in text field | Other - please specify in text field-Sticky joints, damper stuck at duct wall | Air duct | Adjust
90349422 | 2016-01-17 | A081-0S8361A | SDU SCROLL MOTOR 0SM-8361A2 MOTOR FAULT | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10183607 | 700001730110 | ABB | Electrical | 13438.52 | 443 | 425 | Overload / overcurrent | Overload / overcurrent-Motor taking high current | Bearings | Repair / correct
90349870 | 2016-01-07 | A081-2A8324 | LEAK.SW,PIN,FFU TO BIO 3 HOSE* | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10182438 | 700002297332 |  | Integrity | 0 | 0 | 0
90350121 | 2016-01-06 | A081-1S0241 | 1S0241 filter element to be replaced | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10184335 | 700002354895 | JFC CORPORATION | Integrity | 1930.56 | 61 | 14 |  | - | Filter cartridges
90351179 | 2016-02-02 | A081-1F5111 | 1F-5111, L ROW WINDOW GLASS DAMAGED | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10184759 | 700002348459 | KTI | Integrity | 531.32 | 50 | 19 | Operating outside design | Operating outside design-excess heat readiation from flapper | Glass section | Replace
90351237 | 2016-01-11 | A081-0P2021 | RECTIFY ACC CLEANING PUMP NOT STARTING | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10184940 | 700002199414 | PRATISSOLI | Rotating | 48.32 | 24 | 0 | Other - please specify in text field | Other - please specify in text field-Reason due to frequent start and stop | Other - please specify in text field | Check/ Inspect/ Test
90351642 | 2016-01-12 | A081-294XA-50200-S | 294XA50200 ELECT TRACING COMMON FUALT | MX04 | I_MIS_PFC | Emergency | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10185039 | 700002607282 |  | Instrumentation | 117.18 | 4 | 0 | Hardware / Software failure | Hardware / Software failure-Value exceeds set for thermostat | Cable and associated components | Check/ Inspect/ Test
90351643 | 2016-01-14 | A081-1S0241 | 1S-0241 FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10185059 | 700002354895 | JFC CORPORATION | Integrity | 1436.5 | 10 | 14 |  | - | Filter cartridges
90351722 | 2016-01-16 | A081-294XA-50200-S | To rectify alarm of 2ET-LPU-070 | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10185051 | 700002607282 |  | Instrumentation | 3128.06 | 133 | 83 | Software / Hardware fault | Software / Hardware fault-thermostate faulty | Heating element | Replaced
90351823 | 2016-02-18 | A081-2A8324 | FFU 2 NDE REAR INNER WHEEL WIGGLING* | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10185161 | 700002297332 |  | Integrity | 0 | 0 | 98
90352119 | 2016-01-19 | A081-1F5111 | Rev Code_Earth Correction 151LP5111 | MX04 | M_FUR_X | Routine Wrk Lvl 1 | 0 |  | SMR FURNACE | CM | LPU | 10185252 | 700002348459 | KTI | Integrity | 23.08 | 10 | 8 | Power failure | Power failure-To avoid floating power supply | Other - please specify in text field | Modify
90352208 | 2016-01-19 | A081-0S0163A | 0S-0163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10185433 | 700002200042 | DKME | Integrity | 3788.46 | 50 | 37 |  | - | Filter cartridges
90352467 | 2016-01-19 | A081-0S0163A | 0S-163A flare line 1st isolation valve | MX04 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10185594 | 700002200042 | DKME | Integrity | 376.28 | 20 | 41 |  | - | Change over valve
90352479 | 2016-01-22 | A081-1S0241 | 1S-0241 DP high filter replace reqd | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10185576 | 700002354895 | JFC CORPORATION | Integrity | 1985.1 | 63 | 14 |  | - | Filter cartridges
90352736 | 2016-01-20 | A081-0P2021 | PROVIDE ELECTRICAL CONNECTION ACCCLEAN | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10185741 | 700002199414 | PRATISSOLI | Rotating | 117.17 | 16 | 0 | Other - please specify in text field | Other - please specify in text field-As per Operation requirement | Belt Drive | Fix / Repair
90352946 | 2016-02-01 | A081-0P2021 | PROVIDE ELECTRICAL CONNECTION ACCCLEAN | MX04 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10185867 | 700002199414 | PRATISSOLI | Rotating | 121.6 | 70 | 12
90353014 | 2016-01-21 | A081-294XA-50200-S | 294XA50200 ele tracing cmn fail- EHT | MX04 | I_MIS_PFC | Emergency | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10185901 | 700002607282 |  | Instrumentation | 0 | 13 | 17 | Software / Hardware fault | Software / Hardware fault-redandent Thermostat faulty | Heating element | Check/ Inspect/ Test
90353177 | 2016-02-01 | A081-294XA-50200-S | 2ET-LPU-070 Redundant thrmostat replace | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10185949 | 700002607282 |  | Instrumentation | 1861.36 | 66 | 83 | Software / Hardware fault | Software / Hardware fault-thermostate faulty | Heating element | Replaced
90353360 | 2016-01-25 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10186062 | 700002200043 | DKME | Integrity | 3758.1 | 48 | 37 |  | - | Filter cartridges
90353384 | 2016-02-01 | A081-0S8361A | LEAK, WATER, SDU A, NDE, FEED SIDE* | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10185969 | 700001729713 |  | Rotating | 0 | 0 | 0
90353441 | 2016-02-20 | A081-0P2021 | PROVIDE ELECTRICAL CNNECTN ACC CLEAN* | MX04 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10185868 | 700002199414 | PRATISSOLI | Rotating | 1147.1 | 120 | 22
90353613 | 2016-01-25 | A081-1S0241 | 1S-0241 DP high filter replace reqd | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10186182 | 700002354895 | JFC CORPORATION | Integrity | 1889.6 | 51 | 14 |  | - | Filter cartridges
90354620 | 2016-01-31 | A081-1F5111 | 1F5111 PEEP HOLE GLASS COVER BROCKEN | MX04 | M_FUR_X | Routine Wrk Lvl 1 | 0 |  | SMR FURNACE | CM | LPU | 10186518 | 700002348459 | KTI | Integrity | 0 | 16 | 24 | Operating outside design | Operating outside design-excess heat readiation from flapper | Glass section | Replace
90354622 | 2016-02-01 | A081-1S0241 | 1S-0241 DP high, need element replace | MX09 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10186487 | 700002354895 | JFC CORPORATION | Integrity | 1363.9 | 0 | 8 |  | - | Filter cartridges
90354757 | 2016-02-04 | A081-1F5111 | 1F-5111 D-12 BURNER DAMPER BRACE LOOSE | MX04 | M_FUR_X | Routine Wrk Lvl 1 | 0 |  | SMR FURNACE | CM | LPU | 10186520 | 700002348459 | KTI | Integrity | 119.78 | 0 | 7 | Normal Wear | Normal Wear-bolt loose | Dampers | Fix / Repair
90354758 | 2016-02-14 | A081-1F5111 | SMR1 PENTHOUSE PLATFORM GRATING LOOSE | MX04 | M_FUR_X | Routine Wrk Lvl 1 | 0 |  | SMR FURNACE | CM | LPU | 10186517 | 700002348459 | KTI | Integrity | 231.32 | 9 | 10 | Other - please specify in text field | Other - please specify in text field-loose | Furnace grating | Fix / Repair
90355637 | 2016-02-20 | A081-1F5111 | FS1F5111 BNR I-10 VIEGLASS SCREW MISSNG | MX04 | M_FUR_X | Routine Wrk Lvl 2 | 0 |  | SMR FURNACE | CM | LPU | 10187300 | 700002348459 | KTI | Integrity | 50.32 | 8 | 8 | Material defect | Material defect- | Floor of radiant section | Replace
90355669 | 2016-02-17 | A081-0P2021 | ASU7 CLEANING KIT IS FAULTY 0P-2021* | MX04 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10187296 | 700002199414 | PRATISSOLI | Rotating | 176.55 | 8 | 10 | Misalignment | Misalignment-not moving upside | Other - please specify in text field | Adjust / align
90356123 | 2016-02-11 | A081-0S0163A | High delta pressure across 0S-0163A.. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10187585 | 700002200042 | DKME | Integrity | 3894.95 | 64 | 37 |  | - | Filter cartridges
90356684 | 2016-02-23 | A081-0P2021 | PROVIDE ELECTRICAL CONNECTION ACCCLEAN | MX09 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10188027 | 700002199414 | PRATISSOLI | Rotating | 6305.9 | 602 | 571 | Design Error | Design Error-cable connection requirement | Belt Drive | Fix / Repair
90356994 | 2016-02-22 | A081-294XA-50200-S | 2ET-LPU-084 Defective thermostat EHT | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10188092 | 700002607282 |  | Instrumentation | 5296.01 | 62 | 183 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replaced
90357234 | 2016-03-05 | A081-1A8324 | 1A-8324 SCRAPPER WHEEL STRUCK UP* | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10187732 | 700002348718 |  | Integrity | 205.48 | 32 | 10 | Other - please specify in text field | Other - please specify in text field-wheel damaged | Other - please specify in text field | Fix / Repair
90357366 | 2016-06-30 | A081-294XA-50200-S | 2ET-LPU-HD-2- 21SW7101911 2R4001 | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10188403 | 700002607282 |  | Instrumentation | 3242.03 | 121 | 313 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90357563 | 2016-06-29 | A081-294XA-50200-S | 2SB400E5-19 EHT FAULT(3rd) 2ET-LPU-HD-02 | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10188485 | 700002607282 |  | Instrumentation | 3777.45 | 28 | 183 | Software / Hardware fault | Software / Hardware fault-thermostat malfunction | Heating element | Check/ Inspect/ Test
90357905 | 2016-06-28 | A081-294XA-50200-S | 2ET-LPU-071 2SW-7402221 4700RV PLATFORM | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10188696 | 700002607282 |  | Instrumentation | 3014.41 | 33 | 69 | Software / Hardware fault | Software / Hardware fault-thermostat malfunction | Heating element | Check/ Inspect/ Test
90358085 | 2016-02-26 | A081-1S0241 | 1S-0241 Filter DP Hi,element to be repl | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10188766 | 700002354895 | JFC CORPORATION | Integrity | 465.94 | 44.5 | 14 |  | - | Filter cartridges
90358091 | 2016-03-19 | A081-294XA-50200-S | 2ET-LDF-031 2SW7300832 | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10188821 | 700002607282 |  | Instrumentation | 0 | 0 | 0
90358310 | 2016-02-29 | A081-0S0163B | High Delta pressure across 0S-0163B. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10188998 | 700002200043 | DKME | Integrity | 4264.61 | 70.5 | 37 |  | - | Filter cartridges
90358788 | 2016-03-11 | A081-1S0241 | 1S-0241 Filter DP Hi,element to be repl | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10189170 | 700002354895 | JFC CORPORATION | Integrity | 0.01 | 0 | 14 |  | -
90359106 | 2016-03-27 | A081-1F5111 | 1F5111 BURNER CLEANING 1 to 8 E, F & G | MX09 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10189368 | 700002348459 | KTI | Integrity | 976.9 | 85 | 512 | Coking | Coking-BURNER CHOKED | Burner - cup throat | Fix / Repair
90359356 | 2016-03-03 | A081-0P2021 | RECTIFY UNLOADERVALVE ISSUE-ACC CLEANING | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10189657 | 700002199414 | PRATISSOLI | Rotating | 11534.05 | 29 | 13 | Other - please specify in text field | Other - please specify in text field- | Other - please specify in text field | Replace
90359357 | 2016-03-07 | A081-0P2021 | RECTIFY LIMIT SWITCH ISSUE-ACC CLEANING | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10189656 | 700002199414 | PRATISSOLI | Rotating | 51.36 | 12 | 0 | Other - please specify in text field | Other - please specify in text field-cable loose connections | Other - please specify in text field | Other - please specify in text field
90359782 | 2016-03-12 | A081-0P2021 | PRESSURE TESTING OF ACC SUCTION HOSE | MX09 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10189853 | 700002199414 | PRATISSOLI | Rotating | 463.18 | 0 | 30 | Other - please specify in text field | Other - please specify in text field-Periodical test | Other - please specify in text field | Check/ Inspect/ Test
90360304 | 2016-06-12 | A081-2SB210N2 | Flood Light not Function in BB area | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10188923 | 700002373562 | ABB MALAYSIA | Electrical | 494.37 | 40 | 20 | Other - please specify in text field | Other - please specify in text field-LIFE TIME FINISHED | Lamps | Check/ Inspect/ Test
90360649 | 2016-03-15 | A081-0S0123A | 0S-0123A FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10190333 | 700002201322 | DKME | Integrity | 3848.65 | 36 | 37 |  | - | Filter cartridges
90360687 | 2016-03-27 | A081-1SB210N2 | 1LFN210N201L104 TO BE DISSCONNECT | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10190302 | 700002352082 | ABB MALAYSIA | Electrical | 282.21 | 26 | 70 | Operating outside design | Operating outside design- | Lamps | Repair / correct
90360823 | 2016-03-17 | A081-0S8361A | MSDU FEED PUMP OVERLOAD TRIP | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10190436 | 700001729713 |  | Rotating | 312.92 | 40 | 10 | Product Contamination | Product Contamination-Pump struck up | Rotating element | Replace
90361259 | 2016-03-20 | A081-0P2021 | ATTEND ELECTRICAL FAULT ON 0PM-2021 | MX04 | M_PUM_RECI | Emergency | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10190770 | 700002199414 | PRATISSOLI | Rotating | 132.45 | 10 | 0
90361345 | 2016-04-03 | A081-1SB220N2 | FlOOD LIGHTS NOT WORKING AROUND AFR043 | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10190706 | 700002356603 | ABB MALAYSIA | Electrical | 170.38 | 8 | 56 | Other - please specify in text field | Other - please specify in text field-ageing | Lamps | Replaced
90361464 | 2017-06-05 | A081-0S8361A | MSDU FEED PUMP OVERHAULING REF:90360823 | MX20 |  | Routine Wrk Lvl 4 | 0 |  | CENTRIFUGE | CM | ETP |  |  |  |  | 362.98 | 16 | 0
90362601 | 2016-04-14 | A081-1F5111 | 1F5111 BNR F1 CRACK, NEED REPLACEMNT | MX04 | M_FUR_X | Routine Wrk Lvl 2 | 0 |  | SMR FURNACE | CM | LPU | 10191547 | 700002348459 | KTI | Integrity | 2637.11 | 78 | 41 | Material defect | Material defect- | Burner - cup throat | Replace
90362602 | 2016-04-19 | A081-1F5111 | 1F5111 OBSERVN WINDOW-B FLAPPER STUCKED | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10191541 | 700002348459 | KTI | Integrity | 74.11 | 6 | 10 | Fouling | Fouling-Window move out of center,whn operting | Other - please specify in text field | Adjust
90362619 | 2016-05-01 | A081-0P2021 | HOSE TAG FABRICATION | MX04 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10191443 | 700002199414 | PRATISSOLI | Rotating | 190.1 | 32 | 32 | Other - please specify in text field | Other - please specify in text field-New Hoses | Other - please specify in text field | Fix / Repair
90363017 | 2016-04-03 | A081-0S8361A | FS-SDU A 0SM-8361A MOTOR FAULT | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10191803 | 700001730109 | ABB | Electrical | 180.38 | 5 | 4 | Overload / overcurrent | Overload / overcurrent-due to overload | Invertor | Check/ Inspect/ Test
90363584 | 2016-04-07 | A081-1A8324 | PH1 DAF SCRAPPER 1A-8324 NDE REAR WHEEL | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10192145 | 700002348718 |  | Integrity | 117.03 | 40 | 0 | Other - please specify in text field | Other - please specify in text field-wheel damaged | Bund / bunded area | Replace
90364026 | 2016-04-11 | A081-0S8361A | MSDU POLYMER SPEED CNTRL KNOB NT WOKNG | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10192616 | 700001729713 |  | Rotating | 94.51 | 12 | 0 | Fouling | Fouling-found knob come out from grip | Instrumentation | Fix / Repair
90364031 | 2016-04-26 | A081-0S8361A | MSDU ENTRANCE DOOR NOT CLOSING | MX04 | M_ROT_CENT | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10192617 | 700001729713 |  | Rotating | 504.12 | 40 | 40 |  | -NO PPM
90364077 | 2016-04-20 | A081-0P2021 | PROVIDE FITTING FOR POWER WASHER SUCTION | MX09 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10192636 | 700002199414 | PRATISSOLI | Rotating | 3049.09 | 32 | 49 | Other - please specify in text field | Other - please specify in text field-New Pump for Operation | Other - please specify in text field | Fix / Repair
90364078 | 2016-04-13 | A081-0P2021 | INSPECTION OF POWER WASHER ASU | MX09 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10192633 | 700002199414 | PRATISSOLI | Rotating | 290.95 | 8 | 8
90365339 | 2016-05-03 | A081-1SB220N2 | 1LFN220N208L201 Light not glowing. | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10193270 | 700002356603 | ABB MALAYSIA | Electrical | 180.51 | 8 | 8 | Mechanical damage | Mechanical damage- | Lamps | Replaced
90365353 | 2016-04-19 | A081-0S0163A | High delta pressure across 0S-0163A. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10193298 | 700002200042 | DKME | Integrity | 3807.75 | 40 | 45 |  | - | Filter cartridges
90365370 | 2016-04-23 | A081-2A8324 | 2A-8324 NON DRIVE END WHEEL DAMAGE | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10193268 | 700002297332 |  | Integrity | 876.42 | 124 | 124 | Other - please specify in text field | Other - please specify in text field-wheel damaged | Bund / bunded area | Replace
90365658 | 2016-05-22 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX04 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10193577 | 700002200043 | DKME | Integrity | 0 | 0 | 45 |  | -
90365665 | 2016-06-20 | A081-0S0163B | MX-09 0S-0163B filter replacement | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10193605 | 700002200043 | DKME | Integrity | 4198.18 | 44 | 45 | Other - please specify in text field | Other - please specify in text field-Due to DP is high | Filter medium | Replace
90365913 | 2016-04-25 | A081-0S8361A | SDU CENTRIFUGE MOTOR FAULT | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10193790 | 700001730109 | ABB | Electrical | 0 | 4 | 4 | Software / Hardware fault | Software / Hardware fault-Overload as operation side- Blocked | Control Circuit | Repair / correct
90366245 | 2016-04-26 | A081-0S0163B | HC filter 0S-0163-B replace | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10193882 | 700002200043 | DKME | Integrity | 3824.96 | 37.5 | 48 |  | - | Filter cartridges
90366367 | 2016-05-17 | A081-2SB210N2 | 2E-3041 ELECTRICAL WORK TO BE COMPLETE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10194318 | 700002373562 | ABB MALAYSIA | Electrical | 1340.86 | 61 | 306 | Other - please specify in text field | Other - please specify in text field-removed for MTA-2 for Maintenance job | Cable / Terminations | Other - please specify in text field
90367156 | 2016-05-02 | A081-0X0104 | FS-0XM 104 high amp troubleshooting | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | SCREW CONVEYOR | CM | FGP | 10194819 | 700002203439 | DRM LOHER | Electrical | 70.94 | 4 | 4 | Overload / overcurrent | Overload / overcurrent- | Other - please specify in text field | Check/ Inspect/ Test
90367411 | 2016-05-04 | A081-0S8361A | MSDU MACERATOR PUMP SUSPECTED JAMMED | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10194838 | 700001729713 |  | Rotating | 0 | 24 | 8 | Fouling | Fouling-foreign particles found | Rotating element | Fix / Repair
90367412 | 2016-05-10 | A081-0X0104 | 0X-0104 required cleaning | MX04 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10194840 | 700002206193 |  | Electrical | 83.33 | 6 | 10 | Fouling | Fouling-Fouling | Rotating element | Cleaned
90367629 | 2016-05-12 | A081-294XA-50200-S | ETLPU-071 2SW7402221 heat tracing failur | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10194630 | 700002607282 |  | Instrumentation | 2949.96 | 36 | 108 | Software fault | Software fault-out of calibration thermostat | Heat Tracing | Field repair
90367780 | 2016-05-15 | A081-0S0163A | Hydrocarbon filter 0S-0163-A Replace | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10195095 | 700002200042 | DKME | Integrity | 4615.21 | 50 | 48 |  | - | Filter cartridges
90368035 | 2016-05-08 | A081-294XA-50200-S | 294XA50200 ele tracing cmn fail- HSE EHT | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10195371 | 700002607282 |  | Instrumentation | 153.07 | 18 | 18 | Hardware / Software failure | Hardware / Software failure-earth leakage tripping | Controller | Check/ Inspect/ Test
90368264 | 2016-06-16 | A081-0S0163B | High delta pressure across 0S-0163 B. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10195444 | 700002200043 | DKME | Integrity | 3962.79 | 57 | 46 |  | -Due to DP is high | Filter cartridges
90368265 | 2016-05-14 | A081-0S0123B | High delta pressure across 0S-0123 B. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10195443 | 700002200643 | DKME | Integrity | 4136.41 | 53 | 46 |  | - | Filter cartridges
90368546 | 2016-05-21 | A081-0S8361A | MSDU TUBE LIGHT INSIDE CABIN BUSTED | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10195540 | 700001729713 |  | Rotating | 539.85 | 40 | 6 | Other - please specify in text field | Other - please specify in text field-tube light failed | Other - please specify in text field | Replace
90368582 | 2016-05-26 | A081-294XA-50200-S | 294XA50200 ELECT.TRACING FAIL 2ET-LPU-60 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10195582 | 700002607282 |  | Instrumentation | 2296.47 | 20 | 132 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault-Earth leakage | Heat Tracing | Field repair
90368632 | 2016-05-11 | A081-1SB220N2 | LIGHT DIFFUSER DAMAGED -SGP FINFAN AREA | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10195673 | 700002356603 | ABB MALAYSIA | Electrical | 2047 | 56 | 0 | Mechanical damage | Mechanical damage- | Lighting Fixture | Repair / correct
90369286 | 2016-05-15 | A081-0S0143A | 0S-0143A filter replacement job | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10196100 | 700002201324 | DKME | Integrity | 3981.64 | 34 | 43 |  | - | Filter cartridges
90369314 | 2016-05-25 | A081-294XA-50200-S | 294XA50200 ELECT.TRACING FAIL 2ET-LPU-34 | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10195924 | 700002607282 |  | Instrumentation | 32.22 | 20 | 20 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault-Earth leakage | Heat Tracing | Disconnect / Reconnect
90369465 | 2016-05-17 | A081-1SB210N2 | LIGHT FIXTURES DAMAGED-AA/AB FINFAN AREA | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10196159 | 700002352082 | ABB MALAYSIA | Electrical | 402.88 | 38 | 80 | Mechanical damage | Mechanical damage- | Lighting Fixture | Repair / correct
90369742 | 2016-06-11 | A081-294XA-50200-S | 294XA50200 ELECTTRACING FAIL 2ET-LPU-53 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10196350 | 700002607282 |  | Instrumentation | 1195.96 | 71 | 314 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault-earth leakage relay activated | Heat Tracing | Field repair
90369861 | 2016-06-07 | A081-294XA-50200-S | 294XA50200 elect.tracing.fail 2ET-LPU-15 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10196373 | 700002607282 |  | Instrumentation | 844.71 | 102 | 395 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault-earth leakage relay activate | Heat Tracing | Other - please specify in text field
90370030 | 2016-05-19 | A081-294XA-50200-S | 294XA50200 ELECT.RACING FAIL 2SB400E9-Q2 | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10196375 | 700002607282 |  | Instrumentation | 0 | 5 | 0 | Software fault | Software fault-tripped after start up | Heat Tracing | Other - please specify in text field
90370188 | 2016-05-22 | A081-1SB220N2 | 1LFN220N201L222 DIFFUSER DAMAGED | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL |  | 700002356603 | ABB MALAYSIA | Electrical | 0 | 0 | 0
90370189 | 2016-05-31 | A081-1SB220N2 | 1LFN220N201L222 DIFFUSER DAMAGED | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10196497 | 700002356603 | ABB MALAYSIA | Electrical | 103.17 | 8 | 8 | Mechanical damage | Mechanical damage-S/F PIPE HIT THE LAMPS WHILE ERECTING | Lamps | Replace
90370447 | 2016-05-28 | A081-294XA-50200-S | 294XA50200 EHT FAULT 2ETLPU033 | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10196791 | 700002607282 |  | Instrumentation | 3965.48 | 69 | 149 | Incorrect setting/calibration | Incorrect setting/calibration-thermostat trip | Heat Tracing | Hardware Replacement
90370681 | 2016-05-26 | A081-0S8361A | MSDU POLYMER PUMP SUCTION SPOOL BROKEN | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10196835 | 700001729713 |  | Rotating | 204.02 | 42 | 36 | Normal Wear | Normal Wear-suction spool broken | Other - please specify in text field | Replace
90370879 | 2016-05-24 | A081-0S0143B | 0S-0143B FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10196928 | 700002202402 | DKME | Integrity | 3949.28 | 40.5 | 43
90371044 | 2016-05-26 | A081-0S8361A | FS SDU CENTRIFUGE A MOTOR FAULT | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10197084 | 700001730109 | ABB | Electrical | 299.54 | 8 | 8 | Overload | Overload-Overload as operation side- Blocked | Protection Relay / MCU | Repair / correct
90371196 | 2016-05-29 | A081-1S0241 | 1S-0241 dp is high filter replacment req | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10197217 | 700002354895 | JFC CORPORATION | Integrity | 1551.3 | 19 | 20
90371511 | 2016-06-06 | A081-294XA-50200-S | 2ET-LPU-097 EHT FAULT 2V8843 | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10197418 | 700002607282 |  | Instrumentation | 3012.79 | 81 | 231 | Incorrect setting/calibration | Incorrect setting/calibration-thermostat controler faulty | Heat Tracing | Hardware Replacement
90371574 | 2016-06-16 | A081-1SB220N2 | LIGHTS NOT WOKRING IN FNGR-2 GROUNDFLOOR | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10197208 | 700002356603 | ABB MALAYSIA | Electrical | 627.42 | 23 | 12 | Operating at high temperature | Operating at high temperature- | Switch / Isolator | Adjust / reset
90371782 | 2016-06-13 | A081-0S8361A | LEAK,SEAL,MSDU POLYMER PUMP | MX04 | M_ROT_CENT | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10195189 | 700001729713 |  | Rotating | 0 | 0 | 0
90372135 | 2016-06-14 | A081-0S0163B | Hydrocarbon filter 0S-0163-B | MX04 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10197527 | 700002200043 | DKME | Integrity | 0 | 0 | 0
90372141 | 2016-07-22 | A081-0S0123A | Hydrocarbon filter 0S-0123-A | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10197525 | 700002201322 | DKME | Integrity | 0 | 0 | 43 |  | - | Filter cartridges
90372142 | 2016-06-18 | A081-0S0143A | Hydrocarbon filter 0S-0143-A | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10197526 | 700002201324 | DKME | Integrity | 4151.25 | 63 | 43 | Other - please specify in text field | Other - please specify in text field-dp is high | Filter cartridges | Replace
90373026 | 2016-06-23 | A081-1A8324 | RETA PH1 FFU DRIVE END WHEEL WIGGLING | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10197739 | 700002348718 |  | Integrity | 6247.67 | 138 | 120 | Normal Wear | Normal Wear-wheel damaged | Rotating element | Replace
90373229 | 2016-06-26 | A081-2SB200N2 | BA AREA LIGHTING OFF | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10198260 | 700002373557 | ABB MALAYSIA | Electrical | 653.94 | 42 | 12 | Other - please specify in text field | Other - please specify in text field-LIFE TIME FINISHED | Lamps | Check/ Inspect/ Test
90373253 | 2016-06-08 | A081-0S8361A | MSDU ELECTRICAL FAULT TO BE RESET | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10198308 | 700001730109 | ABB | Electrical | 32.23 | 10 | 0 | Leakage | Leakage-BREAKER TRIP | Control Circuit | Adjust / reset
90373419 | 2016-06-09 | A081-294XA-50200-S | TR2 ET-LDF-021 EHT CMFAIL ALARM- HSE | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10198358 | 700002607282 |  | Instrumentation | 3052.78 | 62 | 183 | Incorrect setting/calibration | Incorrect setting/calibration-thermostat controller activated | Heat Tracing | Field repair
90373555 | 2016-06-11 | A081-294XA-50200-S | TR2 ET-LPU-089 FAULT BOTH MAIN&REDUNT | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10198448 | 700002607282 |  | Instrumentation | 424.15 | 26 | 412 | Incorrect setting/calibration | Incorrect setting/calibration-thermostat controller activated | Heat Tracing | Field repair
90373701 | 2016-06-25 | A081-2SB200N2 | LIGHT NOT WORKING ABOVE 2K-3201 | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10198418 | 700002373557 | ABB MALAYSIA | Electrical | 205.72 | 10 | 18 | Mechanical damage | Mechanical damage-LIFE TIME FINISHED | Lamps | Check/ Inspect/ Test
90373883 | 2016-06-20 | A081-1SB220N2 | LIGHTS OFF AT FINFAN / ELVATED PLATFORM | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10198449 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 0 | 0
90373904 | 2016-06-13 | A081-1A8324 | PH1 DAF NEW SKIMMER WHEELS DAMAGED | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10198739 | 700002348718 |  | Integrity | 187.06 | 8 | 0 | Other - please specify in text field | Other - please specify in text field-wheel damage | Other - please specify in text field | Other - please specify in text field
90374039 | 2016-03-01 | A081-0S0143B | 0S-0143-B inlet second valve free wheel | MX04 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10198783 | 700002202402 | DKME | Integrity | 711.48 | 38 | 68 | Mechanical damage | Mechanical damage-Worn wheel stopper damaged,cover damaged | Other - please specify in text field | Replace
90374285 | 2016-06-14 | A081-0S0163A | High delta pressure across 0S-0163A.. | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10198918 | 700002200042 | DKME | Integrity | 4189.47 | 63 | 43 | Other - please specify in text field | Other - please specify in text field-dp is high | Other - please specify in text field | Replace
90374569 | 2016-06-30 | A081-294XA-50200-S | 2ET-LPU-087COMMON ELECTRICAL FAULT EHT | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10199035 | 700002607282 |  | Instrumentation | 4383.98 | 59 | 183 | Software / Hardware fault | Software / Hardware fault-thermostat malfunction | Heating element | Replace
90374907 | 2016-07-14 | A081-294XA-50200-S | 2ET-LDF-023 HEAT TRACING FAULT ALARM | MX04 |  | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10199247 |  |  |  | 4226.07 | 77 | 209 | Software / Hardware fault | Software / Hardware fault-thermostat malfunction | Heating element | Replace
90374912 | 2016-07-01 | A081-0X0104 | 0X-104 screw conveyer cleaning required. | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10199167 | 700002206193 |  | Electrical | 157.5 | 10 | 10 | Other - please specify in text field | Other - please specify in text field-Screw conveyor choked | Other - please specify in text field | Cleaned
90375118 | 2016-06-26 | A081-1A8324 | FFU-1 DAF SCUM BOARD RUBBER DAMAGED | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10199440 | 700002348718 |  | Integrity | 209.97 | 22 | 22 | Normal Wear | Normal Wear-rubber damaged | Bolting and Gaskets | Replace
90375153 | 2016-07-18 | A081-2SB210N2 | BUSTED FLOODLIGHT (2R3021-29)_PENDANT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199414 | 700002373562 | ABB MALAYSIA | Electrical | 993.6 | 47 | 134 | Mechanical damage | Mechanical damage-LIFE TIME FINISHED | Lamps | Replace
90375154 | 2017-01-01 | A081-2SB210N2 | BUSTED FLOODLIGHT (2R3021-29)_STRUCTURE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199415 | 700002373562 | ABB MALAYSIA | Electrical | 3936.88 | 143 | 540 | end of life | end of life- | Lamps | Replace
90375155 | 2017-06-15 | A081-2SB210N2 | BUSTED FLOOD LIGHT AT BB AREA 1st FLOOR | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199394 | 700002373562 | ABB MALAYSIA | Electrical | 2217.77 | 100 | 438 | end of life | end of life- | Lamps | Replace
90375156 | 2016-08-14 | A081-2SB210N2 | BUSTED FLOOD LIGHT AT BB AREA 2nd FLOOR | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199395 | 700002373562 | ABB MALAYSIA | Electrical | 1193.78 | 54 | 304 | Mechanical damage | Mechanical damage-LIFE TIME FINISHED | Lamps | Replace
90375157 | 2017-06-15 | A081-2SB210N2 | BUSTED FLOOD LIGHT AT BB AREA 3rd FLOOR | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199398 | 700002373562 | ABB MALAYSIA | Electrical | 1291.42 | 50 | 262 | end of life | end of life- | Lamps | Replace
90375159 | 2016-10-15 | A081-2SB210N2 | BB -COMP. HOUSE_BUSTED CEILING LIGHT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199424 | 700002373562 | ABB MALAYSIA | Electrical | 1331.57 | 44 | 154 | Mechanical damage | Mechanical damage- | Lamps
90375160 | 2016-10-09 | A081-2SB210N2 | BB -COMP. HOUSE_BUSTED STRUCTURE LIGHT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199426 | 700002373562 | ABB MALAYSIA | Electrical | 838.37 | 27 | 172 | end of life | end of life- | Lamps | Replace
90375162 | 2017-06-01 | A081-2SB210N2 | BUSTED FLOODLIGHT (2R3021-29)_PENDANT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199505 | 700002373562 | ABB MALAYSIA | Electrical | 1354.23 | 72 | 532 | end of life | end of life- | Lamps | Replace
90375163 | 2016-07-19 | A081-2SB210N2 | BB -U23400 AREA_BUSTED STRUCTURE LIGHT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199545 | 700002373562 | ABB MALAYSIA | Electrical | 832.19 | 16 | 212 | Mechanical damage | Mechanical damage-LIFE TIME FINISHED | Lamps | Replace
90375380 | 2016-06-26 | A081-1A8324 | RETA PH1 DAF NEW BRIDGE WHEEL DAMAGE | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10199566 | 700002348718 |  | Integrity | 152.17 | 8 | 6 | Normal Wear | Normal Wear-Bridge wheel damaged | Other - please specify in text field | Replace
90375579 | 2016-07-18 | A081-2SB210N2 | BB PIPERACK BOTTOM FLOOR. LAMPS CKT-01 | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199666 | 700002373562 | ABB MALAYSIA | Electrical | 869.76 | 24 | 92 | Mechanical damage | Mechanical damage-LIFE TIME FINISHED | Lamps | Replace
90375580 | 2016-07-25 | A081-2SB210N2 | BB PIPERACK BOTTOM FLOOR. LAMPS CKT-02 | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199668 | 700002373562 | ABB MALAYSIA | Electrical | 1169.62 | 51 | 85 | Mechanical damage | Mechanical damage-LIFE TIME FINISHED | Lamps | Replace
90375581 | 2016-07-23 | A081-2SB210N2 | BB PIPERACK BOTTOM FLOOR. LAMPS CKT-03 | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10199672 | 700002373562 | ABB MALAYSIA | Electrical | 1088.51 | 27 | 77 | Mechanical damage | Mechanical damage-LIFE TIME FINISHED | Lamps | Replace
90375749 | 2016-06-25 | A081-0S0143B | 0S-143B, DP high need to replace filter | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10199886 | 700002202402 | DKME | Integrity | 4365.97 | 94.5 | 43
90375877 | 2016-06-26 | A081-0S0143B | 0S-143B filters to be clean | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200037 | 700002202402 | DKME | Integrity | 17400.89 | 8 | 43 | Product Contamination | Product Contamination- | Filter cartridges | Replace
90375950 | 2016-06-26 | A081-0S0163A | 0S-0163A FILTER REPLACEMENT REQD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200038 | 700002200042 | DKME | Integrity | 92.28 | 0 | 43 | Product Contamination | Product Contamination- | Filter cartridges | Replace
90376110 | 2016-06-27 | A081-0S0163B | 0S-163B DP high | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200016 | 700002200043 | DKME | Integrity | 4462.68 | 36 | 43 |  | - | Filter cartridges
90376233 | 2016-06-27 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200015 | 700002201324 | DKME | Integrity | 234.69 | 8 | 43 | Product Contamination | Product Contamination- | Filter cartridges | Replace
90376234 | 2016-06-27 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200047 | 700002201322 | DKME | Integrity | 189.19 | 4 | 43 | Product Contamination | Product Contamination- | Filter cartridges | Replace
90376235 | 2016-07-28 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200048 | 700002200643 | DKME | Integrity | 4998.26 | 0 | 43
90376236 | 2016-06-28 | A081-0S0163A | OS-0163A HC filter element replacment | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200046 | 700002200042 | DKME | Integrity | 279.49 | 8 | 43 | Product Contamination | Product Contamination- | Filter cartridges | Replace
90376237 | 2016-06-27 | A081-0S0163B | 0S-163B DP high | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200241 | 700002200043 | DKME | Integrity | 443.05 | 8 | 43 | Product Contamination | Product Contamination- | Filter cartridges | Replace
90376238 | 2016-06-27 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200304 | 700002201324 | DKME | Integrity | 307.78 | 28 | 43 |  | - | Filter cartridges
90376258 | 2016-06-27 | A081-0S0163A | 0S-163A DP HIGH | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200326 | 700002200042 | DKME | Integrity | 4545.84 | 37.5 | 43 |  | - | Filter cartridges
90376455 | 2016-08-11 | A081-2SB200N2 | BA AREA_LIGHTING GRND LEVEL_ALWAYS ON | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10200329 | 700002373557 | ABB MALAYSIA | Electrical | 1363.41 | 10 | 136 | end of life | end of life- | Other - please specify in text field | Check/ Inspect/ Test
90376473 | 2016-06-28 | A081-0S0163B | 0S-163B DP high | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200435 | 700002200043 | DKME | Integrity | 351.9 | 33.5 | 43 |  | - | Filter cartridges
90376474 | 2016-06-28 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200434 | 700002202402 | DKME | Integrity | 288.89 | 24 | 43 |  | - | Filter cartridges
90376654 | 2016-06-29 | A081-0S0163A | 0S-163A DP HIGH | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200517 | 700002200042 | DKME | Integrity | 11478.05 | 40 | 43 |  | - | Filter cartridges
90376655 | 2016-06-29 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200519 | 700002201324 | DKME | Integrity | 353.9 | 33.5 | 43 | Product Contamination | Product Contamination-product contamination | Filter cartridges | Replace
90377171 | 2016-07-04 | A081-0S0123B | OS-0123B filter element replacment | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200818 | 700002200643 | DKME | Integrity | 374.7 | 100 | 43 |  | - | Filter cartridges
90377176 | 2016-07-03 | A081-0S0163B | High Delta pressure across 0S-0163B. | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200793 | 700002200043 | DKME | Integrity | 476.17 | 45 | 43 |  | - | Filter cartridges
90377189 | 2016-09-13 | A081-2SB200N2 | BA PIPERACK BOTTOM FLOUR LAMPS CKT-01&02 | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10200659 | 700002373557 | ABB MALAYSIA | Electrical | 1198.34 | 54 | 140 | Mechanical damage | Mechanical damage-LIFE TIME FINISHED | Lamps | Replace
90377190 | 2016-07-04 | A081-2A8324 | PH2 FFU SCAPPER 2A-8324 COMMON ALARM | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10200815 | 700002297890 | ABB | Electrical | 925.28 | 18 | 18 | Other - please specify in text field | Other - please specify in text field-Motor temperature alarm | Other - please specify in text field | Other - please specify in text field
90377191 | 2016-09-26 | A081-2SB200N2 | BA REACTORS BOTTOM AREA FLOUR.LAMPS | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10200679 | 700002373557 | ABB MALAYSIA | Electrical | 618.64 | 44 | 160 | Mechanical damage | Mechanical damage-LIFE TIME FINISHED | Lamps | Replace
90377192 | 2017-06-21 | A081-2SB200N2 | BA AREA ALL UNITS BUSTED STRUCTURE LIGHT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10200682 | 700002373557 | ABB MALAYSIA | Electrical | 3886.45 | 150 | 702 | end of life | end of life- | Lamps | Replace
90377195 | 2016-07-17 | A081-294XA-50200-S | 2ET-LDF-026,2SW7300631,2U-4300 EHT FAULT | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10200805 | 700002607282 |  | Instrumentation | 1698.46 | 100 | 219 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90377197 | 2016-07-11 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200819 | 700002200042 | DKME | Integrity | 4285.06 | 41 | 43 |  | - | Filter cartridges
90377388 | 2017-05-04 | A081-0S0143A | 0S-0143A Repair of iso valve gearbox | MX04 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200884 | 700002201324 | DKME | Integrity | 0 | 0 | 16 |  | -
90377399 | 2016-07-18 | A081-0P2021 | PRESSURE TESTING ACC CLEANING HOSES - HP | MX04 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10200895 | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 0
90377400 | 2016-07-18 | A081-0P2021 | PRESSURE TESTING ACC CLEANING HOSES - LP | MX04 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10200894 | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 0
90377403 | 2016-07-05 | A081-0S0123A | High delta pressure across 0S-0123A. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10200855 | 700002201322 | DKME | Integrity | 306.95 | 38 | 43 |  | - | Filter cartridges
90377429 | 2016-07-13 | A081-294XA-50200-S | 2ET-LPU-077, 2U4700, EHT FAULT | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10200879 | 700002607282 |  | Instrumentation | 2930.39 | 96 | 115 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault-thermostat malfunction | Heat Tracing | Hardware Replacement
90377900 | 2016-07-21 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201097 | 700002201324 | DKME | Integrity | 3773.06 | 8 | 43
90377901 | 2016-07-14 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201098 | 700002202402 | DKME | Integrity | 3933.08 | 20 | 43 |  | - | Filter cartridges
90377902 | 2016-07-13 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201099 | 700002200042 | DKME | Integrity | 2843.54 | 44 | 43 |  | - | Filter cartridges
90377904 | 2016-07-14 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201100 | 700002200043 | DKME | Integrity | 3955.61 | 24 | 43 |  | - | Filter cartridges
90377905 | 2016-07-30 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201096 | 700002200643 | DKME | Integrity | 29260.34 | 0 | 43
90377906 | 2016-07-29 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201095 | 700002201322 | DKME | Integrity | 3911.32 | 24 | 43 |  | - | Filter cartridges
90377918 | 2016-07-20 | A081-294XA-50200-S | TR2 ET-LPU-002 heat tracing alarm 2R4001 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10201149 | 700002607282 |  | Instrumentation | 5554.97 | 99 | 229 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90377921 | 2016-07-14 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201200 | 700002201324 | DKME | Integrity | 2831.13 | 32 | 43 |  | - | Filter cartridges
90377922 | 2016-07-09 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201201 | 700002202402 | DKME | Integrity | 289 | 29 | 43 |  | - | Filter cartridges
90378282 | 2016-07-12 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201308 | 700002200043 | DKME | Integrity | 2970.97 | 53 | 43 |  | - | Filter cartridges
90378501 | 2016-10-05 | A081-294XA-50200-S | EHT FAULT 2ET-LDF-027 TR2 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10201310 | 700002607282 |  | Instrumentation | 5007.74 | 87 | 219 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90378776 | 2016-07-18 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201537 | 700002200042 | DKME | Integrity | 4119.52 | 28 | 43 |  | - | Filter cartridges
90378777 | 2016-08-03 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201538 | 700002201324 | DKME | Integrity | 3957.11 | 22 | 43 |  | - | Filter cartridges
90378899 | 2016-07-14 | A081-0S0163A | FS-0S-0163A vent to flare valve faulty | MX04 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201597 | 700002200042 | DKME | Integrity | 95.34 | 10 | 7 | Normal Wear | Normal Wear-Normal Wear | Other - please specify in text field | Fix / Repair
90378906 | 2016-07-13 | A081-294XA-50200-S | 294XA50200 Elect alarm _ 2SB 400 E05 | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10201606 | 700002607282 |  | Instrumentation | 46.87 | 6 | 0 | Leakage | Leakage-ELR tripped | Fuse / MCB | Check/ Inspect/ Test
90379028 | 2016-08-07 | A081-0P2021 | PRESSURE TEST OF WAT & ACC CLEANINGHOSES | MX09 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10201637 | 700002199414 | PRATISSOLI | Rotating | 1726.7 | 192 | 192 | Other - please specify in text field | Other - please specify in text field-PRESSURE TEST OF WAT & ACC CLEANINGHOSES | Other - please specify in text field | Calibrate
90379543 | 2016-08-02 | A081-0X0104 | 0X-0104 conveyor to be cleaned. | MX04 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10201990 | 700002206193 |  | Electrical | 0 | 4 | 12 | Fouling | Fouling-Choked screw conveyor | Rotating element | Cleaned
90379561 | 2016-07-24 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201941 | 700002202402 | DKME | Integrity | 4108.71 | 36 | 43 |  | - | Filter cartridges
90379563 | 2016-07-19 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201940 | 700002200043 | DKME | Integrity | 4030.92 | 27 | 43 |  | - | Filter cartridges
90379568 | 2016-07-21 | A081-0S0163A | OS-0163A filter element replacment | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10201939 | 700002200042 | DKME | Integrity | 3765.85 | 20 | 43 |  | - | Filter cartridges
90379935 | 2016-10-09 | A081-294XA-50200-S | TR2 LPU EHT 50 FAULT | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10202121 | 700002607282 |  | Instrumentation | 5285.65 | 75 | 82 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90380098 | 2016-07-24 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202207 | 700002200043 | DKME | Integrity | 4086.04 | 21 | 43 |  | - | Filter cartridges
90380381 | 2016-07-28 | A081-0S0143B | 0S-0143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202419 | 700002202402 | DKME | Integrity | 268.56 | 0 | 43 | Product Contamination | Product Contamination- | Filter cartridges | Replace
90380545 | 2016-07-29 | A081-0S0143A | 0S-0143A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202481 | 700002201324 | DKME | Integrity | 527.1 | 24 | 43 |  | - | Filter cartridges
90380546 | 2016-07-28 | A081-0S0163A | 0S-0163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202480 | 700002200042 | DKME | Integrity | 103.13 | 15 | 43 |  | - | Filter cartridges
90380547 | 2016-07-31 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202478 | 700002200043 | DKME | Integrity | 770.86 | 27 | 43 |  | - | Filter cartridges
90381004 | 2016-07-01 | A081-0S0143A | 0S-0143A DP high, filter to be replaced | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202811 | 700002201324 | DKME | Integrity | 3661.59 | 0 | 43
90381007 | 2016-08-13 | A081-0S0163B | 0S-0163B DP high, filter to be replaced | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202810 | 700002200043 | DKME | Integrity | 1848.38 | 36 | 43 |  | - | Filter cartridges
90381016 | 2016-08-13 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202776 | 700002200042 | DKME | Integrity | 3742.32 | 32 | 43 |  | - | Filter cartridges
90381036 | 2016-08-20 | A081-0S0163B | 0S-0163B filter element to be replaced. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202827 | 700002200043 | DKME | Integrity | 1796.95 | 32 | 43 |  | - | Filter cartridges
90381037 | 2016-08-05 | A081-0S0163A | 0S-0163A filter element to be replaced. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202826 | 700002200042 | DKME | Integrity | 305.33 | 46 | 43 |  | - | Filter cartridges
90381038 | 2016-08-01 | A081-0S0143B | 0S-0143B filter element to be replaced. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202830 | 700002202402 | DKME | Integrity | 4042.71 | 27 | 43 |  | - | Filter cartridges
90381039 | 2016-08-07 | A081-0S0123B | 0S-0123B filter element to be replaced. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202829 | 700002200643 | DKME | Integrity | 3983.21 | 16 | 43 |  | - | Filter cartridges
90381040 | 2016-08-01 | A081-0S0123A | 0S-0123A filter element to be replaced. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202828 | 700002201322 | DKME | Integrity | 3754.37 | 16 | 43 |  | - | Filter cartridges
90381264 | 2016-08-10 | A081-0S0143B | 0S-0143B filter element to be replaced. | MX04 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10202831 | 700002202402 | DKME | Integrity | 3868.85 | 20 | 43 |  | - | Filter cartridges
90381461 | 2016-07-31 | A081-0S0143A | High delta pressure across 0S-0143A. | MX04 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10203032 | 700002201324 | DKME | Integrity | 229.68 | 16 | 43 |  | - | Filter cartridges
90381462 | 2016-07-31 | A081-0S0123A | High delta pressure across 0S-0123A. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10203030 | 700002201322 | DKME | Integrity | 6591.67 | 20 | 43 |  | - | Filter cartridges
90381630 | 2016-08-01 | A081-0X0104 | 0X-0104 extruder motor reset required. | MX04 | M_PAC_CON2 | Schedule Breaker | 0 |  | SCREW CONVEYOR | CM | FGP | 10203056 | 700002206193 |  | Electrical | 2190.24 | 32 | 18 | Software / Hardware fault | Software / Hardware fault-Internal fault | Control Circuit | Replace
90381632 | 2016-08-02 | A081-294XA-50200-S | 2ET-LPU-071 TR2 U4700 EHT FAULT- HSE | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10203085 | 700002607282 |  | Instrumentation | 3616.09 | 118 | 138 | Software / Hardware fault | Software / Hardware fault-thermostat malfunction | Heating element | Replace
90381939 | 2016-08-28 | A081-1SB210N2 | isolate the lighting fixtures on AB area | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10203129 | 700002352082 | ABB MALAYSIA | Electrical | 509.57 | 59 | 62
90381956 | 2016-08-02 | A081-0S0163B | High Delta pressure across 0S-0163B. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10203203 | 700002200043 | DKME | Integrity | 3000.24 | 24 | 43 |  | - | Filter cartridges
90381982 | 2016-07-01 | A081-0S0123A | High delta pressure across 0S-0123A. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10203215 | 700002201322 | DKME | Integrity | 0 | 0 | 0
90382093 | 2016-08-05 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10203292 | 700002201324 | DKME | Integrity | 304.72 | 28 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90382301 | 2016-08-16 | A081-0S0163A | 0S-0163A FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10203423 | 700002200042 | DKME | Integrity | 6829.61 | 36 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90382302 | 2016-08-14 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10203421 | 700002200043 | DKME | Integrity | 4618.46 | 36 | 43 |  | - | Filter cartridges
90382499 | 2016-08-14 | A081-0X0104 | 0X-0104 conveyor cleaning /attend leak | MX04 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10203574 | 700002206193 |  | Electrical | 0 | 0 | 12 | Product Contamination | Product Contamination-Cellulose become hard in humid atmospher | Rotating element | Cleaned
90382586 | 2016-09-04 | A081-1SB220N2 | LIGHT DIFFUSER DAMAGED SGP REACTOR AREA | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10203387 | 700002356603 | ABB MALAYSIA | Electrical | 518.36 | 8 | 8 | end of life | end of life- | Lighting Fixture
90382587 | 2016-09-04 | A081-1SB210N2 | LIGHT DIFFUSER DAMAGED AT AB AREA(U3400) | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10203393 | 700002352082 | ABB MALAYSIA | Electrical | 393.2 | 6 | 6 | end of life | end of life- | Lighting Fixture | Replace
90382594 | 2016-08-15 | A081-0S0123A | High delta pressure across 0S-0123A. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10203602 | 700002201322 | DKME | Integrity | 482.55 | 40 | 43 |  | - | Filter cartridges
90382760 | 2016-12-11 | A081-1SB210N2 | LIGHT DIFFUSER DAMAGED AT HPS-1, AB AREA | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10203608 | 700002352082 | ABB MALAYSIA | Electrical | 4553.66 | 68 | 152 | Mechanical damage | Mechanical damage- | Lamps
90383280 | 2016-08-19 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10204108 | 700002200043 | DKME | Integrity | 5684.58 | 36 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90383281 | 2016-05-01 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10204107 | 700002200643 | DKME | Integrity | 476.65 | 32 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90383551 | 2016-08-22 | A081-294XA-50200-S | 2ET-LDF-027 EHT alarm | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10204337 | 700002607282 |  | Instrumentation | 0 | 0 | 0
90383623 | 2016-08-22 | A081-0S0163B | 0S-163B DP high, need to replace | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10204375 | 700002200043 | DKME | Integrity | 440.67 | 45 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90383624 | 2016-08-16 | A081-0S0123A | 0S-123A DP high, need to replace | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10204373 | 700002201322 | DKME | Integrity | 450.23 | 36 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90383625 | 2016-08-22 | A081-0S0143A | 0S-143A DP high, need to replace | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10204372 | 700002201324 | DKME | Integrity | 440.67 | 45 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90384036 | 2016-08-28 | A081-0S0163A | 0S-163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10204532 | 700002200042 | DKME | Integrity | 6207 | 32 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90384123 | 2016-09-08 | A081-1A8324 | PH1 DAF SCUM BOARD RUBBER DAMAGED | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10203777 | 700002348718 |  | Integrity | 1948.73 | 117 | 117 | Product Contamination | Product Contamination-Scrapper leakage | Other - please specify in text field | Replace
90384128 | 2016-10-02 | A081-294XA-50200-S | 294XA50200 common fault alam LPU-EHT-033 | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10204034 | 700002607282 |  | Instrumentation | 5709.73 | 72 | 178 | Operating at high temperature | Operating at high temperature-process temp high | Heating element | Check/ Inspect/ Test
90384581 | 2016-09-08 | A081-0S8361A | SDU 0S-8361A BELLOW DAMAGED | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10203811 | 700001729713 |  | Rotating | 2644.93 | 19 | 19 | Other - please specify in text field | Other - please specify in text field-bellow damage | Other - please specify in text field | Replace
90384665 | 2016-08-22 | A081-0S0163B | 0S-0163B filter element replacment | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10205081 | 700002200043 | DKME | Integrity | 441.12 | 28 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90384825 | 2016-08-24 | A081-1A8324 | DAF1 SCRAPER BRIDGE SMALL WHEEL DAMAGE | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10205211 | 700002348718 |  | Integrity | 1701.79 | 28 | 28 | Other - please specify in text field | Other - please specify in text field-Drive wheel damage | Bund / bunded area | Replace
90385221 | 2016-08-24 | A081-0S0123A | 0S-123A DP high, need to replace | MX09 |  | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10205397 |  |  |  | 4006.69 | 28 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90385595 | 2016-11-12 | A081-2SB210N2 | LIGHTING COVER DAMAGE (23 NOS.)_BB AREA | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10205539 | 700002373562 | ABB MALAYSIA | Electrical | 5437.4 | 51 | 58 | Mechanical damage | Mechanical damage- | Lamps
90385629 | 2016-09-08 | A081-2A8324 | RETA DAFph2 scraper small wheel damage | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10205285 | 700002297332 |  | Integrity | 187 | 22 | 22 | Normal Wear | Normal Wear-wheel damaged | Rotating element | Replace
90385635 | 2016-09-04 | A081-0S0163B | High Delta pressure across 0S-0163B. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10205511 | 700002200043 | DKME | Integrity | 4260.6 | 28 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90385714 | 2016-09-05 | A081-0S0163A | High delta pressure across 0S-0163A. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10205848 | 700002200042 | DKME | Integrity | 4264.12 | 20 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90385931 | 2016-09-28 | A081-0S8361A | SDU CENTRIFUGE A BELLOW REPAIR | MX04 | M_ROT_CENT | Routine Wrk LvL 5 | 0 |  | CENTRIFUGE | CM | ETP | 10205789 | 700001729713 |  | Rotating | 0 | 0 | 0
90386681 | 2016-09-03 | A081-0S0123B | 0S-0123B DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10206366 | 700002200643 | DKME | Integrity | 4284.58 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90386969 | 2016-09-24 | A081-1SB220N2 | LIGHTING MCB TRIPPING_AC AREA | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10206484 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 0 | 13 | Software / Hardware fault | Software / Hardware fault-Lighting Ballast | Lamps | Replace
90387008 | 2016-09-27 | A081-0S0163B | High Delta pressure across 0S-0163B. | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10206470 | 700002200043 | DKME | Integrity | 4257.37 | 30 | 43 |  | - | Filter cartridges
90387012 | 2016-09-24 | A081-2SB200N2 | BA exchanger side All floorPoor Lighting | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10205574 | 700002373557 | ABB MALAYSIA | Electrical | 165.54 | 4 | 4 | Overload | Overload-MCB TRIP 2SB200N2,CKT-14 | Lamps | Adjust / reset
90387438 | 2016-09-06 | A081-0S8361A | MSDU CENTRIFUGE DEAFULT ELECTRICAL FAULT | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10206739 | 700001729713 |  | Rotating | 126.61 | 12 | 12 | Power / other utility failure | Power / other utility failure-Bowl-VSDS tripped on Overcurrent-Fault | Instrumentation | Fix / Repair
90387868 | 2017-03-05 | A081-0P2021 | PROCURE ACC CLEANING HOSE-1SUCTION 1DIS | MX09 | M_PUM_RECI | Routine Wrk LvL 5 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10206958 | 700002199414 | PRATISSOLI | Rotating | 1720.69 | 0 | 0 | Normal Wear | Normal Wear-ACC CLEANING HOSE PROCURE | Other - please specify in text field | Other - please specify in text field
90388224 | 2016-10-13 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10207142 | 700002201322 | DKME | Integrity | 4015.87 | 20 | 43 |  | - | Filter cartridges
90388729 | 2016-09-15 | A081-0P2021 | REPAIR DAMAGE FITTING OF POWER WASHER | MX09 | M_PUM_RECI | Emergency | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10207399 | 700002199414 | PRATISSOLI | Rotating | 90.91 | 0 | 0 | Poor installation | Poor installation- | Other - please specify in text field | Fix / Repair
90389182 | 2016-09-28 | A081-2A8324 | RETA PH2 DAF NEW BRIDGE WHEEL DAMAGE | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10207573 | 700002297332 |  | Integrity | 1097.03 | 23 | 23 | Normal Wear | Normal Wear-wheel damaged | Rotating element | Replace
90389189 | 2016-10-02 | A081-0S8361A | RETA,LEAK WAT, CASING, MSDU CENT PUMP*R | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10205180 | 700001729713 |  | Rotating | 483.43 | 4 | 86 | Normal Wear | Normal Wear- | Rotating element | Fix / Repair
90389537 | 2017-07-10 | A081-1F5111 | PROCURE SPW GASKETS 1F-5111 TUBE-SDREQ | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10207786 | 700002348459 | KTI | Integrity | 0 | 2 | 1
90389661 | 2016-10-10 | A081-2SB200N2 | LIGHT DIFFUSER DAMAGED AT HPS-2 ,BA AREA | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10207837 | 700002373557 | ABB MALAYSIA | Electrical | 896.64 | 12 | 52 | Mechanical damage | Mechanical damage- | Lamps
90390173 | 2016-10-06 | A081-0S8361A | MSDU INSIDE CONAINER LIGHT NOT WORKING | MX04 | E_MOT_LV | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10208122 | 700001730109 | ABB | Electrical | 119.74 | 6 | 6 | end of life | end of life- | Other - please specify in text field | Replace
90390605 | 2016-09-30 | A081-0S0123B | 0S-123B DP HIGH | MX04 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10208263 | 700002200643 | DKME | Integrity | 3998.37 | 24 | 43 |  | - | Filter cartridges
90391056 | 2016-10-22 | A081-294XA-50200-S | 2ET-LPU-001 FAULT ALARM- 2SW7302211- TR2 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10208361 | 700002607282 |  | Instrumentation | 3071.12 | 80 | 192 | Other - please specify in text field | Other - please specify in text field-thermostat faulty | Heat Tracing | Hardware Replacement
90391830 | 2016-10-11 | A081-0S0163A | High delta pressure across 0S-163A. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10208826 | 700002200042 | DKME | Integrity | 4257.72 | 32 | 43 |  | - | Filter cartridges
90391837 | 2017-01-14 | A081-294XA-50200-S | EHT TR2 fault alarm 2ET-LPU-099 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10208869 | 700002607282 |  | Instrumentation | 4088.05 | 120 | 234 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90392395 | 2016-10-11 | A081-0S8361A | MSDU CENT PUMP OH,REF WO#90389189 | MX20 |  | Routine Wrk Lvl 4 | 0 |  | CENTRIFUGE | CM | ETP |  |  |  |  | 3268.01 | 80 | 240
90393669 | 2016-10-20 | A081-0S0163B | High Delta pressure across 0S-0163B. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10209818 | 700002200043 | DKME | Integrity | 3815.88 | 24 | 43 |  | - | Filter cartridges
90394665 | 2016-11-06 | A081-294XA-50200-S | TR2 U4700 ET-LPU-070 EHT FAULT | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10210275 | 700002607282 |  | Instrumentation | 133.29 | 46 | 46 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90394684 | 2016-10-27 | A081-0S0123B | High delta pressure across 0S-0123B. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10210280 | 700002200643 | DKME | Integrity | 3878.71 | 24 | 43 |  | - | Filter cartridges
90395232 | 2016-11-05 | A081-1A8324 | pHASE-1 DAF scum board support pipe dama | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10210436 | 700002348718 |  | Integrity | 1101.96 | 97 | 97 | Normal Wear | Normal Wear-Support pipe broken | Bund / bunded area | Fix / Repair
90395233 | 2016-11-06 | A081-1A8324 | RETA DAF SCRAPPER WHEEL UN BALANCED | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10210192 | 700002348718 |  | Integrity | 2552.9 | 28 | 28 | Normal Wear | Normal Wear-Bridge wheel damaged | Bund / bunded area | Replace
90395234 | 2016-11-03 | A081-0S0163A | 0S-0163 A filter to be replacement | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10210534 | 700002200042 | DKME | Integrity | 3817.93 | 24 | 43 |  | - | Filter cartridges
90395989 | 2016-11-08 | A081-294XA-50200-S | FS-2ET-LDF-HD06 alarm | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10210932 | 700002607282 |  | Instrumentation | 54.92 | 4 | 4 | Software / Hardware fault | Software / Hardware fault-thermostat alarm | Heating element | Adjust / reset
90396002 | 2016-11-01 | A081-1S0241 | 1S-0241 DP high filter element repl-OPRQ | MX04 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10210970 | 700002354895 | JFC CORPORATION | Integrity | 1631.35 | 21 | 46 |  | - | Filter cartridges
90396417 | 2016-11-12 | A081-294XA-50200-S | FS-2ETLPU HD-03 both main & Red ON Alarm | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10211148 | 700002607282 |  | Instrumentation | 124.51 | 4 | 4 | Software / Hardware fault | Software / Hardware fault- | Heating element | Check/ Inspect/ Test
90396564 | 2017-05-28 | A081-0S0123A | 0S-0123A INLET VALVE INSULATION TO BE RE | MX04 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10211292 | 700002201322 | DKME | Integrity | 0 | 0 | 53
90397146 | 2016-11-17 | A081-294XA-50200-S | 2ET-LPU-HD-3 Main/Red. thermostat alarm. | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10211199 | 700002607282 |  | Instrumentation | 503.5 | 17 | 142 | Software / Hardware fault | Software / Hardware fault-thermostat suspected | Heating element | Check/ Inspect/ Test
90397160 | 2016-12-20 | A081-0S8361A | Leak, water, drop, MSDU water storage ta | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10211628 | 700001729713 |  | Rotating | 305.1 | 26 | 130 | Normal Wear | Normal Wear-Gasket damaged | Bolting and Gaskets | Replace
90397349 | 2016-11-15 | A081-0S0123A | High DP across 0S-0123A. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10211719 | 700002201322 | DKME | Integrity | 3935.88 | 32 | 43 |  | - | Filter cartridges
90397632 | 2016-11-12 | A081-0S0163B | High DP across 0S-0163B. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10211853 | 700002200043 | DKME | Integrity | 3908.4 | 28 | 43 |  | - | Filter cartridges
90398342 | 2016-11-14 | A081-2SB210N2 | LIGHT DIFFUSER DAMAGED BB AREA | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10212208 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 6 | 6 | Mechanical damage | Mechanical damage- | Lamps | Replace
90398343 | 2016-11-20 | A081-2SB210N2 | FLOOD LIGHT REFLECTOR HANGING - BB AREA | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10212209 | 700002373562 | ABB MALAYSIA | Electrical | 138.03 | 10 | 38 | Mechanical damage | Mechanical damage- | Lamps | Repair / correct
90398697 | 2016-11-17 | A081-0S0143A | 0S-0143A filter replacement | MX04 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10212599 | 700002201324 | DKME | Integrity | 4018.16 | 36 | 43 |  | - | Filter cartridges
90398698 | 2016-11-17 | A081-0S0143B | 0S-0143B FILTER REPLACEMENT | MX04 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10212600 | 700002202402 | DKME | Integrity | 4060.84 | 32 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90398835 | 2016-11-24 | A081-0S0163A | 0S-0163 A filter to be replacement | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10212630 | 700002200042 | DKME | Integrity | 4049.73 | 44 | 42 | Product Contamination | Product Contamination- | Filter medium | Replace
90398836 | 2016-12-01 | A081-0S0163B | 0S-0163B HC filter element need to repl | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10212631 | 700002200043 | DKME | Integrity | 3792.32 | 20 | 42 | Product Contamination | Product Contamination- | Filter medium | Replace
90398837 | 2016-07-01 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10212629 | 700002201322 | DKME | Integrity | 3553.85 | 0 | 42 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90398839 | 2016-11-29 | A081-0S0123B | OS-0123B HC filter element replacement | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10212633 | 700002200643 | DKME | Integrity | 3843.81 | 24 | 42 | Product Contamination | Product Contamination- | Filter medium | Replace
90399472 | 2016-11-26 | A081-1SB220N2 | POOR LIGHT IN FINFAN AREA | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10213013 | 700002356603 | ABB MALAYSIA | Electrical | 70.92 | 6 | 4 | Mechanical damage | Mechanical damage- | Lamps | Adjust / reset
90399678 | 2016-01-02 | A081-1SB220N2 | Tube light AD pipe rack top not glowing | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10213123 | 700002356603 | ABB MALAYSIA | Electrical | 51.57 | 4 | 4 | Internal failure / short | Internal failure / short- | Fuse / MCB | Adjust / reset
90399860 | 2016-12-05 | A081-0S0163A | 0S-0163 A filter to be replacement | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10213150 | 700002200042 | DKME | Integrity | 324 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90400150 | 2016-12-07 | A081-0P2021 | PROCURE ACC CLEANING PUMP HOSES & CABLES | MX04 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU |  | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 0
90400365 | 2017-03-09 | A081-0P2021 | PROCURE ACC CLEANING PUMP HOSES & CABLES | MX09 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10213353 | 700002199414 | PRATISSOLI | Rotating | 11764.64 | 2 | 2 | Normal Wear | Normal Wear- | Seals (other than mechanical) | Replace
90400370 | 2016-12-04 | A081-0P2021 | PROCURE TOOLS FOR OPERATIONS | MX09 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10213356 | 700002199414 | PRATISSOLI | Rotating | 1736.97 | 0 | 80
90400517 | 2016-11-27 | A081-294XA-50200-S | EHT 294XA-50200-S COMMON FAULT ALARM | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10213421 | 700002607282 |  | Instrumentation | 46.87 | 4 | 4 | Other - please specify in text field | Other - please specify in text field-high temp alarm | Heating element | Check/ Inspect/ Test
90400679 | 2016-12-05 | A081-0S0143A | 0S-0143A filter replacement | MX04 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10213510 | 700002201324 | DKME | Integrity | 3943.74 | 26 | 43 | Product Contamination | Product Contamination- | Filter cartridges | Replace
90400716 | 2016-11-27 | A081-1SB210N2 | TO CHCEK / REPAIR LIGHT FIXTURES | MX04 | E_SWB_D | Emergency | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10213666 | 700002352082 | ABB MALAYSIA | Electrical | 268.19 | 36 | 8 | Ingress of water / condensation | Ingress of water / condensation- | Lamps
90400853 | 2016-12-28 | A081-0S0143A | 0S-0143A filter replacement | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10213707 | 700002201324 | DKME | Integrity | 21582.56 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90400891 | 2016-12-13 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10213736 | 700002202402 | DKME | Integrity | 3778.81 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90401178 | 2016-12-15 | A081-294XA-50200-S | EHT 294XA-50200-S COM FLT AL 2ET-LPU-HD3 | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10213750 | 700002607282 |  | Instrumentation | 3377.1 | 73 | 150 | Software / Hardware fault | Software / Hardware fault-thermostat suspected | Heating element | Replace
90401365 | 2016-12-01 | A081-1A8324 | DAF 1 DE SCRAPER NEED ADDITIONAL SUPPORT | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10213912 | 700002348718 |  | Integrity | 410.27 | 56 | 63 | Other - please specify in text field | Other - please specify in text field-poor skimming | Other - please specify in text field | Fix / Repair
90401380 | 2016-12-29 | A081-1A8324 | RETA NDE FRONT INNER WHEEL WOBBLING | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10213359 | 700002348718 |  | Integrity | 779.3 | 188 | 94
90401390 | 2016-12-06 | A081-0S0123B | 0S-0123B FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10213865 | 700002200643 | DKME | Integrity | 264.07 | 20 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90401392 | 2016-12-14 | A081-0S0163B | 0S-0163B filter replacement | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10213866 | 700002200043 | DKME | Integrity | 3862.74 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90402145 | 2016-12-18 | A081-0S0123A | High DP across 0S-0123A. | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10214283 | 700002201322 | DKME | Integrity | 185.61 | 16 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90402161 | 2016-12-10 | A081-294XA-50200-S | 2ET-LDF-002 TRACING ALARM EHT-HSE | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10214183 | 700002607282 |  | Instrumentation | 3368.54 | 73 | 187 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90402548 | 2016-12-06 | A081-0S0163A | 0S-163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10214433 | 700002200042 | DKME | Integrity | 211.26 | 16 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90402704 | 2017-01-17 | A081-0S0123B | 0S-123B DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10214490 | 700002200643 | DKME | Integrity | 3553.85 | 0 | 43
90402706 | 2016-12-28 | A081-0S0163A | 0S-163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10214489 | 700002200042 | DKME | Integrity | 3895.28 | 28 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90403262 | 2017-01-03 | A081-0S0163B | High DP across 0S-0163B. | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10214864 | 700002200043 | DKME | Integrity | 2643.99 | 44 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90403264 | 2016-12-25 | A081-0S0123A | High DP across 0S-0123A. | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10214863 | 700002201322 | DKME | Integrity | 2561.33 | 0 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90403271 | 2016-12-12 | A081-0S8361A | MSDU electrical fault | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10214771 | 700001730109 | ABB | Electrical | 0 | 0 | 0 | Mechanical damage | Mechanical damage-History capctured in WO-90403435 | Control Circuit | Repair / correct
90403868 | 2016-12-21 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10215282 | 700002201324 | DKME | Integrity | 282.56 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Other - please specify in text field
90403870 | 2016-12-28 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10215247 | 700002202402 | DKME | Integrity | 8895.99 | 36 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90403872 | 2017-01-01 | A081-0X0104 | 0X-104, conveyor to be cleaned. | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10215283 | 700002206193 |  | Electrical | 58.26 | 6 | 12 |  | -Proactive cleaning of screw conveyor | Other - please specify in text field | Cleaned
90404090 | 2016-12-14 | A081-0S0143B | High DP across 0S-0143B. | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10215489 | 700002202402 | DKME | Integrity | 224.01 | 20 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90404091 | 2016-12-14 | A081-0S0123B | High DP across 0S-0123B. | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10215485 | 700002200643 | DKME | Integrity | 251.75 | 20 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90404541 | 2017-01-02 | A081-0P2021 | RETA ACC CLEANING PUMP D/S PRESSURE PH1 | MX04 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10213171 | 700002199414 | PRATISSOLI | Rotating | 98.93 | 44 | 44 | Cavitation | Cavitation- | Other - please specify in text field | Fix / Repair
90404542 | 2017-01-24 | A081-0P2021 | RETA ACC CLEANING PUMP D/S PRESSURE PH2 | MX04 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10213172 | 700002199414 | PRATISSOLI | Rotating | 5003.04 | 52 | 168 | Normal Wear | Normal Wear-Normal Wear | Seals (other than mechanical) | Fix / Repair
90404910 | 2016-12-21 | A081-0S8361A | SDU CFG A BOWL MOTOR TRIP ON MOTOR FAULT | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10215915 | 700001730109 | ABB | Electrical | 0 | 8 | 8 | Overload | Overload-Motor stall | Protection Relay / MCU | Adjust / reset
90404952 | 2017-01-02 | A081-0X0104 | 0X-0104 screw conveyor to be cleaned | MX04 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10215857 | 700002206193 |  | Electrical | 95.33 | 4 | 12 | Other - please specify in text field | Other - please specify in text field-Proactive cleaning of screw conveyor | Other - please specify in text field | Cleaned
90405829 | 2017-01-07 | A081-1A8324 | RETA DAF D/E SMALL WHEEL RUBBER DAMAGE | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10214842 | 700002348718 |  | Integrity | 78.14 | 40 | 20
90406137 | 2017-01-29 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10216506 | 700002200042 | DKME | Integrity | 412.56 | 28 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90406138 | 2017-03-24 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10216507 | 700002200043 | DKME | Integrity | 3571.19 | 0 | 43
90406139 | 2017-03-15 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10216503 | 700002200643 | DKME | Integrity | 0 | 0 | 43
90406140 | 2017-03-25 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10216502 | 700002201322 | DKME | Integrity | 0 | 0 | 43
90406141 | 2017-01-03 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10216504 | 700002201324 | DKME | Integrity | 4046.55 | 40 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90406142 | 2017-01-24 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10216505 | 700002202402 | DKME | Integrity | 2440.42 | 28 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90406494 | 2017-01-04 | A081-0S8361A | RETA MSDU WATER PUMP ABNORMAL NOISE | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10215814 | 700001729713 |  | Rotating | 192.07 | 88 | 88 | Other - please specify in text field | Other - please specify in text field-Seal failed | Mech Seal | Replace
90406703 | 2017-05-29 | A081-0S8361A | MSDU AIR TK KS VALVE AIR PASSING | MX04 | M_ROT_CENT | Routine Wrk LvL 5 | 0 |  | CENTRIFUGE | CM | ETP | 10216821 | 700001729713 |  | Rotating | 23.44 | 9 | 9 | Power / other utility failure | Power / other utility failure-Compressor failed | Instrumentation | Modify
90406985 | 2017-01-24 | A081-0S0143A | 0S-0143A filter replacement | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10216829 | 700002201324 | DKME | Integrity | 3904.86 | 28 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90408686 | 2017-06-29 | A081-0S0163A | 0S-0163A. filter element replacement. | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10217675 | 700002200042 | DKME | Integrity | 16191.77 | 25 | 44 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90409701 | 2017-03-18 | A081-0S0143B | 0S-0143B filter elements to be replaced. | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10218219 | 700002202402 | DKME | Integrity | 411.92 | 32 | 43 | Product Contamination | Product Contamination- | Filter cartridges | Replace
90409712 | 2017-03-16 | A081-0S0143A | 0S-0143A filter replacement, DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10218348 | 700002201324 | DKME | Integrity | 5959.2 | 28 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90410159 | 2017-02-02 | A081-0P2021 | TO DO CABLE CONNECTION FOR ACC CLEANING | MX09 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10218509 | 700002199414 | PRATISSOLI | Rotating | 7927.12 | 457 | 502
90410969 | 2017-01-31 | A081-0X0104 | 0X-104 screw conveyer cleaning | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10218861 | 700002206193 |  | Electrical | 0 | 4 | 12 | Other - please specify in text field | Other - please specify in text field-Proactivly checking fresh batch filtratn | Rotating element | Check/ Inspect/ Test
90410973 | 2017-02-15 | A081-294XA-50200-S | 2ET-LDF-031 ELECTRIC TRACING FAULT EHT* | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10218848 | 700002607282 |  | Instrumentation | 4218.41 | 120 | 234 | Software / Hardware fault | Software / Hardware fault-thermostat suspected | Heating element | Replace
90410988 | 2017-04-06 | A081-1SB210N2 | TEMPORARY LIGHT REMOVAL at AB AREA (29M) | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10218703 | 700002352082 | ABB MALAYSIA | Electrical | 885.41 | 34 | 50
90412526 | 2017-04-04 | A081-294XA-50200-S | 294XA 50200 EHT ALARM 2ETLPUHD10 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10219363 | 700002607282 |  | Instrumentation | 3079.57 | 72 | 122 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90413466 | 2021-11-20 | A081-1F5111 | 1F5111PIGTAIL TUBE INSULATION DAMAGE-SDR | MX04 | M_FUR_X | Routine Wrk LvL 5 | 0 |  | SMR FURNACE | CM | LPU | 10220169 | 700002348459 | KTI | Integrity | 0 | 0 | 6
90413846 | 2017-03-11 | A081-294XA-50200-S | 2ET-LPU-HD-01, EHT FAULT ALARM - TR2 | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10220468 | 700002607282 |  | Instrumentation | 3453.71 | 90 | 204 | Software / Hardware fault | Software / Hardware fault-thermostat suspected | Heating element | Replace
90414241 | 2017-04-18 | A081-0S0143B | 0S-0143B filter replacement, DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10220637 | 700002202402 | DKME | Integrity | 4394.45 | 28 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90414434 | 2017-02-16 | A081-0P2021 | FS Fix 0P2021 ACC cleaning kit pump | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10220860 | 700002199414 | PRATISSOLI | Rotating | 448.37 | 16 | 8 | Power / other utility failure | Power / other utility failure-over load(TOL trip) | Belt Drive | Fix / Repair
90414849 | 2017-03-06 | A081-FIRE HYDRANT | SCE FH475 Valve cap seized - PHASE-1 | MX04 |  | Routine Wrk Lvl 1 | 0 |  | FIRE HYDRANT | CM | UTL | 10220971 |  |  |  | 88.94 | 5 | 5 |  | -REMOVE BLANK CAP, CLEAN IT & FIX BACK
90414851 | 2017-03-06 | A081-FIRE HYDRANT | SCE FH490 Valve cap seized - PHASE-1 | MX04 |  | Routine Wrk Lvl 1 | 0 |  | FIRE HYDRANT | CM | UTL | 10220974 |  |  |  | 46.97 | 5 | 5 |  | -REMOVE BLANK CAP, CLEAN IT & FIX BACK
90414852 | 2017-03-06 | A081-FIRE HYDRANT | SCE FH492 Valve cap seized - PHASE-1 | MX04 |  | Routine Wrk Lvl 1 | 0 |  | FIRE HYDRANT | CM | UTL | 10220975 |  |  |  | 26.18 | 5 | 5 |  | -REMOVE BLANK CAP, CLEAN IT & FIX BACK
90414853 | 2017-03-15 | A081-FIRE HYDRANT | FH485 Outlet gasket needs replaced | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10220977 |  |  |  | 144.73 | 4 | 3 |  | -
90415574 | 2017-01-01 | A081-0S0163B | 0S-0163B filter to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10221560 | 700002200043 | DKME | Integrity | 24474.82 | 26 | 77 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90415575 | 2017-07-27 | A081-0S0123B | 0S-0123B filter to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10221558 | 700002200643 | DKME | Integrity | 1221.75 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90415576 | 2017-07-24 | A081-0S0123A | 0S-0123A filter to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10221555 | 700002201322 | DKME | Integrity | 3790.51 | 24 | 43
90416563 | 2017-03-12 | A081-0P2021 | LEAK WATER ACC CLEAN PUMP PRV BONNET | MX04 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10221982 | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 0
90416574 | 2017-03-12 | A081-0P2021 | ASU6 - ACC CLEANING PUMP DAMAGED PG | MX04 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10221943 | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 0
90417079 | 2017-04-03 | A081-FIRE HYDRANT | SCE:LEAK, GLAND M/VALVE OF FH 491-PH1 | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10222091 |  |  |  | 324.86 | 9 | 10 |  | -Normal Wear
90417080 | 2017-04-04 | A081-FIRE HYDRANT | SCE:LEAK, GLAND M/VALVE OF FH 475-PH-1 | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10222092 |  |  |  | 259.89 | 9 | 10 |  | -Normal Wear
90417083 | 2017-04-04 | A081-FIRE HYDRANT | SCE:LEAK, GLAND M/VALVE OF FH 457-PH-1 | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10222094 |  |  |  | 208.52 | 9 | 10 |  | -Normal Wear
90417403 | 2017-03-04 | A081-0P2021 | LEAK WATER 0P-2021 MANIFOLD | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10222034 | 700002199414 | PRATISSOLI | Rotating | 795.35 | 16 | 17 | Normal Wear | Normal Wear- | Bolting and Gaskets | Fix / Repair
90417445 | 2017-12-21 | A081-0P2021 | ASU-4 LADDER (J/K/L/M SOUTH) REPAIR | MX04 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10222242 | 700002199414 | PRATISSOLI | Rotating | 2634.8 | 32 | 71 | Normal Wear | Normal Wear- | Other - please specify in text field | Other - please specify in text field
90417448 | 2017-08-14 | A081-0P2021 | ASU-3 LADDER (E/F/G/H NORTH) ALIGN | MX04 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10222146 | 700002199414 | PRATISSOLI | Rotating | 0 | 186 | 186 | Other - please specify in text field | Other - please specify in text field-roller misalignment | Other - please specify in text field | Adjust / align
90417812 | 2017-04-02 | A081-FIRE HYDRANT | LEAK, WAT, SEAL, FIRE HYDRANT-130, STG-3 | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10222550 |  |  |  | 55.84 | 28 | 28 | Normal Wear | Normal Wear- | Valve internals | Shop Repair
90419112 | 2017-03-14 | A081-0P2021 | ATTEND 0PM-2021 MOTOR FAULT | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10223463 | 700002199414 | PRATISSOLI | Rotating | 236.2 | 16 | 8 | Thermal growth | Thermal growth-over loaded | Belt Drive | Fix / Repair
90419224 | 2017-04-19 | A081-0S0143A | 0S-0143A filter replacement, DP high | MX09 |  | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10223546 |  |  |  | 4234.73 | 20 | 41 | Product Contamination | Product Contamination- | Filter medium | Replace
90419232 | 2017-04-15 | A081-0P2021 | ATTEND 0PM-2021 LOW OIL LEVEL | MX09 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10223464 | 700002199414 | PRATISSOLI | Rotating | 0 | 10 | 10 | Other - please specify in text field | Other - please specify in text field-low oil level | Lubricator | Fix / Repair
90419302 | 2017-03-16 | A081-0P2021 | To disconnect elect cable from ASU8 and | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10223628 | 700002199414 | PRATISSOLI | Rotating | 714.01 | 54 | 54 | Power / other utility failure | Power / other utility failure-to do the cleaning of acc | Cooling system | Check/ Inspect/ Test
90419566 | 2017-04-24 | A081-1SB220N2 | SGP PH 1 LIGHTING_FAULTY CONTACTOR | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10223587 | 700002356603 | ABB MALAYSIA | Electrical | 382.38 | 4 | 10 | end of life | end of life- | Relay / contactor | Replace
90420133 | 2017-07-10 | A081-0P2021 | REPAIR ACC CLEANING BROKEN BELT | MX04 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10224107 | 700002199414 | PRATISSOLI | Rotating | 976.5 | 32 | 32 | Normal Wear | Normal Wear- | Belt Drive | Replace
90420471 | 2017-03-26 | A081-0P2021 | ACC top cleaning head cntrl cable damage | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10224262 | 700002199414 | PRATISSOLI | Rotating | 890.28 | 64 | 32 | Adverse Weather Conditions | Adverse Weather Conditions-door hitting the cable due to high wind | Cooling system | Replace
90422024 | 2017-04-24 | A081-0P2021 | LEAK, WATER 0P-2021 T-JOINT ASU8 (WELD) | MX04 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10225200 | 700002199414 | PRATISSOLI | Rotating | 43.61 | 156 | 156 | Normal Wear | Normal Wear- | Bolting and Gaskets | Fix / Repair
90422629 | 2017-04-15 | A081-1A8324 | DAF 1 RACKER ARM SUPPORT STEEL ROPE CUT | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10225331 | 700002348718 |  | Integrity | 14127.98 | 16 | 16 | accidental damage | accidental damage-turn buckle broken | Other - please specify in text field | Replace
90422793 | 2018-01-03 | A081-0S8361A | MSDU HVAC COOLING UNIT | MX09 | M_ROT_CENT | Routine Wrk LvL 5 | 0 |  | CENTRIFUGE | CM | ETP | 10225719 | 700001729713 |  | Rotating | 10497.84 | 80 | 121 |  |  |  |  | 09.04.2017 11:21:54 UTC Joseph Maturino (QRJMA2) Clear description of the problem. ADDITIONAL HVAC TO BE PROVIDED IN ETP MSDU AREA. PEFS: T-4.118.415 Prioriteit: Additional mitigations : Requester Name : JOSEPH MATURINO Phone : 44032212 03.01.2018 10:46:17 UTC SYED MUSTAFA (QRSMU7) As per above request for summer mitigation provide Mobile AC Removed mobile hvac after completion
90422901 | 2017-12-23 | A081-2SB210N2 | PM_FLT_PANEL SPACE HEATER-2SB210N2 | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10225020 | 700002373562 | ABB MALAYSIA | Electrical | 940.5 | 8 | 8 | Internal failure / short | Internal failure / short- | Heating element | Replace
90423548 | 2017-12-23 | A081-2SB200N2 | PM_FLT_PANEL SPACE HEATER-2SB200N2 | MX04 |  | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10225914 |  |  |  | 1881 | 12 | 12 | Internal failure / short | Internal failure / short- | Heating element | Replace
90423976 | 2017-09-11 | A081-0S8361A | MSDU DOOR DAMAGED | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10226516 | 700001729713 |  | Rotating | 3607.18 | 0 | 208 |  | -FAILURE OF HINGES/FRAME/LOCKS
90424142 | 2017-05-03 | A081-FIRE HYDRANT | SCE FH025 Butterfly lug missing | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10226576 |  |  |  | 72.06 | 2 | 2 |  | -Butterfly valve lug missing
90424273 | 2017-05-06 | A081-0S0143A | 0S-0143A FILTER TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10226647 | 700002201324 | DKME | Integrity | 525.72 | 36 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90424275 | 2017-04-23 | A081-0S0143B | 0S-0143B FILTER TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10226648 | 700002202402 | DKME | Integrity | 463.4 | 32 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90425013 | 2017-05-06 | A081-294XA-50200-S | 2ET-LDF-04 ELECTRICAL COMMON FAULT ALARM | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10225462 | 700002607282 |  | Instrumentation | 3047.56 | 53 | 131 | Software / Hardware fault | Software / Hardware fault-thermostat suspected | Heating element | Replace
90425741 | 2017-05-18 | A081-1SB220N2 | LIGHT DIFFUSER DAMAGED IN AC P/R AREA | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10227150 | 700002356603 | ABB MALAYSIA | Electrical | 804.49 | 10 | 30 | Mechanical damage | Mechanical damage- | Lamps | Replace
90426224 | 2017-05-16 | A081-2A8324 | DAF 2 SKIMMER BRIDGE SMALL WHEEL DAMAGE | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10227583 | 700002297332 |  | Integrity | 678.76 | 9 | 9
90426412 | 2017-05-10 | A081-2A8324 | PH2 DAF SCRAPPER LINING WORN OUT | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10227705 | 700002297890 | ABB | Electrical | 4080.56 | 120 | 114 | Normal Wear | Normal Wear-wheel assembly worn out | Other - please specify in text field | Replace
90427180 | 2017-05-09 | A081-0P2021 | TO CHECK/RECTIFY ACC CLEANING PUMP ASU8 | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10228044 | 700002199414 | PRATISSOLI | Rotating | 310.22 | 16 | 0 | Power / other utility failure | Power / other utility failure- | Cooling system | Replace
90427888 | 2017-05-14 | A081-0S0143B | 0S-0143B FILTER ELEMENT TO BE REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10228502 | 700002202402 | DKME | Integrity | 4565.46 | 28 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90427905 | 2017-05-21 | A081-0S0143A | 0S-0143A FILTER ELEMENTS TO REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10228503 | 700002201324 | DKME | Integrity | 207.86 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90427990 | 2017-05-29 | A081-FIRE HYDRANT | Deluge Monitor MNZ-58 partially blocked | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10228361 |  |  |  | 0 | 0 | 0
90428024 | 2017-05-16 | A081-0P2021 | Check 0P2021 ACC cleaning pump | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10228576 | 700002199414 | PRATISSOLI | Rotating | 125.87 | 15 | 0 | Power / other utility failure | Power / other utility failure-sensor faulty ,to be replaced | Instrumentation | Replace
90428496 | 2017-06-04 | A081-1SB220N2 | 1LFN220N211L111 LIGHT HAVING WATER | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10227922 | 700002356603 | ABB MALAYSIA | Electrical | 314.74 | 8 | 42 | Ingress of water / condensation | Ingress of water / condensation- | Casing / enclosure | Replace
90428730 | 2017-01-01 | A081-0S0143A | 0S-0143A FILTER TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10228893 | 700002201324 | DKME | Integrity | 297.32 | 34 | 44 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90428746 | 2017-06-20 | A081-FIRE HYDRANT | FH 309 Missing directional lock-% | MX04 |  | Routine Wrk Lvl 4 | 0 |  | FIRE HYDRANT | CM | UTL | 10228782 |  |  |  | 0 | 0 | 6 |  | -
90428753 | 2018-08-24 | A081-FIRE HYDRANT | FIRE HYDRANT - FH-611/614 & FH-593 -% | MX04 |  | Routine Wrk Lvl 4 | 0 |  | FIRE HYDRANT | CM | UTL | 10228783 |  |  |  | 3727.34 | 33 | 33 | Other - please specify in text field | Other - please specify in text field-Normal Wear | Other - please specify in text fields | Replace
90429198 | 2018-01-01 | A081-FIRE HYDRANT | SCE FH332 Valves seized | MX04 |  | Routine Wrk LvL 5 | 0 |  | FIRE HYDRANT | CM | UTL | 10228946 |  |  |  | 4127.94 | 18 | 59 | Product Contamination | Product Contamination-Internal rust and dirt | Valves | Replaced
90429723 | 2017-06-02 | A081-1S0241 | 1S-0241 FILTER ELEMENTS TO BE CLEANED-% | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10229517 | 700002354895 | JFC CORPORATION | Integrity | 1701.17 | 21 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90430323 | 2017-06-15 | A081-FIRE HYDRANT | SCE FH133 5 Inch Outlet Valve Missing | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10226581 |  |  |  | 0 | 0 | 0
90430949 | 2017-06-22 | A081-2SB210N2 | 2LFN210N221L209 DAMAGE DIFUSER REPLACEME | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10233964 | 700002373562 | ABB MALAYSIA | Electrical | 337.45 | 10 | 10 | end of life | end of life- | Lamps | Replace
90431077 | 2017-07-01 | A081-294XA-50200-S | 2LPU-ET-090 EHT FAULT ALARM- 2U4200 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10234577 | 700002607282 |  | Instrumentation | 3272.33 | 62 | 140 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90431409 | 2017-07-11 | A081-0S0143B | 0S-0143B Filter replacement % | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10231634 | 700002202402 | DKME | Integrity | 185.59 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90431465 | 2017-06-17 | A081-0S0163B | 0S-0163B DP high, need to replace % | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10235710 | 700002200043 | DKME | Integrity | 4561.8 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90431469 | 2017-08-30 | A081-0S0163B | 0S-0163 B DP high, need to replace | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10235709 | 700002200043 | DKME | Integrity | 20369.43 | 24 | 48 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90432166 | 2017-06-22 | A081-0X0104 | 0X-104 conveyor to be cleaned- OPRQ | MX04 | M_PAC_CON2 | Schedule Breaker | 0 |  | SCREW CONVEYOR | CM | FGP | 10236085 | 700002206193 |  | Electrical | 56.66 | 52 | 28 | Overload | Overload-Overload due to screw stuck in cellulose | Rotating element | Check/ Inspect/ Test
90432418 | 2017-07-18 | A081-0X0104 | 0X-104 conveyor view glass to repl-% | MX04 | M_PAC_CON2 | Routine Wrk Lvl 4 | 0 |  | SCREW CONVEYOR | CM | FGP | 10236320 | 700002206193 |  | Electrical | 0 | 14 | 14 | Operating outside design | Operating outside design-Cellulose accumulated due to gate closed | mechanical part | Fix / Repair
90432913 | 2017-07-31 | A081-294XA-50200-S | 294XA50200 2-LPU-ET-002 HT FLT ALM MB | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10236724 | 700002607282 |  | Instrumentation | 3102.44 | 55 | 177 | Software / Hardware fault | Software / Hardware fault-MAIN CIRCUIT ECM FAULTY | Heating element | Replace
90433100 | 2017-07-30 | A081-2SB200N2 | BA AREA 2LFN200N218L115 LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10236671 | 700002373557 | ABB MALAYSIA | Electrical | 88.62 | 10 | 31 | end of life | end of life- | Lamps | Replace
90433492 | 2017-07-24 | A081-0S0143B | 0S-143B filter element replacement | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10237114 | 700002202402 | DKME | Integrity | 8705.85 | 24 | 48 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90433493 | 2017-07-29 | A081-0S0163B | 0S-0163B filter to be replaced | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10237118 | 700002200043 | DKME | Integrity | 8355.07 | 44 | 48 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90433494 | 2017-06-28 | A081-0S0163A | 0S-0163A filter to be replaced | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10237105 | 700002200042 | DKME | Integrity | 471.94 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90434563 | 2017-08-16 | A081-0S0163A | 0S-0163A filter element to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10237626 | 700002200042 | DKME | Integrity | 278.33 | 28 | 48 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90434565 | 2017-08-16 | A081-0S0143A | 0S-0143A filter element replace | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10237625 | 700002201324 | DKME | Integrity | 1897.72 | 39 | 48 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90435548 | 2017-07-17 | A081-FIRE HYDRANT | SCE Deluge monitor handle missing TR-2 | MX04 |  | Routine Wrk Lvl 1 | 0 |  | FIRE HYDRANT | CM | UTL | 10238086 |  |  |  | 0 | 0 | 0
90436929 | 2017-07-24 | A081-294XA-50200-S | 294XA50200 2ET-LPU-077 FAULTY* | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10238920 | 700002607282 |  | Instrumentation | 3077.23 | 48 | 162 | Operating at high temperature | Operating at high temperature-process temp high | Heating element | Check/ Inspect/ Test
90437116 | 2017-07-29 | A081-294XA-50200-S | 2ET-LPU-035 Alarm need to check | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10239084 | 700002607282 |  | Instrumentation | 3117.43 | 68 | 182 | Software / Hardware fault | Software / Hardware fault-ECM faulty | Heating element | Replace
90437179 | 2017-07-24 | A081-0S8361A | MSDU Local Fire Alarm Faulty | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10239110 | 700001729713 |  | Rotating | 93.73 | 8 | 8 | Power / other utility failure | Power / other utility failure-low battery | Instrumentation | Replace
90437206 | 2017-07-18 | A081-0S0163A | 0S-163A filter dp high - OPRQ | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10238993 | 700002200042 | DKME | Integrity | 3808.52 | 30 | 48 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90437211 | 2017-07-18 | A081-0S0143B | 0S-143B DP high - OPRQ | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10239228 | 700002202402 | DKME | Integrity | 297.78 | 28 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90437502 | 2017-08-27 | A081-0S0163A | 0S-0163A flare valve lock nut broken -% | MX04 |  | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10239334 |  |  |  | 0 | 15 | 10 | Normal Wear | Normal Wear-Normal Wear | Change over valve | Fix / Repair
90437503 | 2017-07-20 | A081-0S0163B | 0S-0163B filter to be replaced | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10239323 | 700002200043 | DKME | Integrity | 4364.13 | 28 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90437505 | 2017-01-01 | A081-0X0104 | 0X-104 screw conceyor cleaning - % | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10239314 | 700002206193 |  | Electrical | 169.48 | 20 | 40 | Coking | Coking-Bloackage by cellulose | conveyor | Cleaned
90437630 | 2017-08-10 | A081-FIRE HYDRANT | SCE FH551 End cap seized - % | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10239396 |  |  |  | 0 | 6 | 6 | Rust and dirt | Rust and dirt- | Valves | Cleaned
90437638 | 2017-07-21 | A081-0S0143A | 0S-143 A filter element replacement | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10238997 | 700002201324 | DKME | Integrity | 411.82 | 28 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90437666 | 2017-08-15 | A081-0S8361A | MSDU CENTRIFUGE CABIN TWO TUBE LIGHT NOT | MX04 | E_MOT_LV | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10239435 | 700001730109 | ABB | Electrical | 173.47 | 8 | 48 | end of life | end of life-end of life | Other - please specify in text field | Replace
90438125 | 2017-08-04 | A081-0S0143A | 0S-143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10239417 | 700002201324 | DKME | Integrity | 0 | 0 | 43
90438126 | 2017-07-31 | A081-0S0143B | 0S-143B FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10239722 | 700002202402 | DKME | Integrity | 362.97 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90438127 | 2017-08-18 | A081-0S0163B | 0S-163B HC FILTER REPLACEMENT. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10239724 | 700002200043 | DKME | Integrity | 0 | 0 | 43
90438128 | 2017-07-24 | A081-0S0163A | 0S-163A HC FILTER REPLACEMENT. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10239723 | 700002200042 | DKME | Integrity | 411.82 | 32 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90438825 | 2017-09-17 | A081-0S0143B | 0S-143B FILTER ELEMENT REPLACEMENT-% | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10239719 | 700002202402 | DKME | Integrity | 378.67 | 43 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90439878 | 2017-08-20 | A081-2SB210N2 | BB WDU area Normal Light not working | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10240816 | 700002373562 | ABB MALAYSIA | Electrical | 138.43 | 8 | 4 | Internal failure / short | Internal failure / short- | Lamps | Check/ Inspect/ Test
90439880 | 2017-08-28 | A081-2SB200N2 | BA area GF Auto light Sensor malfunction | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10240815 | 700002373557 | ABB MALAYSIA | Electrical | 1520.41 | 12 | 52 | Internal failure / short | Internal failure / short- | Lamps | Replace
90440928 | 2017-08-19 | A081-0S0163B | 0S-163B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10241414 | 700002200043 | DKME | Integrity | 463.4 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90445362 | 2017-09-07 | A081-2A8324 | Phase-2 DAF scrapper motor VSD alarm | MX04 | E_MOT_LV | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10241918 | 700002297890 | ABB | Electrical | 0 | 28 | 28 |  | - | Control Circuit
90445371 | 2017-09-23 | A081-2SB210N2 | BB AREA 2LFN210N2-20-L2-16 LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10241980 | 700002373562 | ABB MALAYSIA | Electrical | 682.45 | 17 | 53 | Insulation failure | Insulation failure- | Lamps | Replace
90445999 | 2017-08-28 | A081-0S0143A | 0S-143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10242056 | 700002201324 | DKME | Integrity | 518.53 | 24 | 43 | Other - please specify in text field | Other - please specify in text field-replace filter element | Filter cartridges | Replace
90449905 | 2017-11-20 | A081-0S0163A | PROC-HYDROCARBON FILTER & GASKETS | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10242807 | 700002200042 | DKME | Integrity | 15180.22 | 0 | 0 | Other - please specify in text field | Other - please specify in text field-PROCUREMENT DONE | Other - please specify in text field
90450094 | 2017-09-04 | A081-0P2021 | TO FIX BROKEN POWER WASH PUMP LANCE ASU6 | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10242870 | 700002199414 | PRATISSOLI | Rotating | 318.74 | 0 | 0 | Other - please specify in text field | Other - please specify in text field-suspect hit moving object (fan blade) | Other - please specify in text field | Fix / Repair
90450743 | 2017-09-06 | A081-0S8361A | MSDU polymer line drain valve damaged | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10243173 | 700001729713 |  | Rotating | 1029.94 | 16 | 16 | Normal Wear | Normal Wear-drain valve is leaking | Other - please specify in text field | Fix / Repair
90450900 | 2017-09-28 | A081-0P2021 | LEAK WATER POWER WASHER PUMP AT ASU 8 | MX04 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10243289 | 700002199414 | PRATISSOLI | Rotating | 977.47 | 4 | 49 | Normal Wear | Normal Wear- | Casing | Check/ Inspect/ Test
90450970 | 2017-11-01 | A081-0S0123A | 0S-123 A filter replace before CS-1 S/up | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10243284 | 700002201322 | DKME | Integrity | 0 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90450979 | 2017-09-14 | A081-0S8361A | MSDU TRIP TO CHECK AND RESET | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10243356 | 700001729713 |  | Rotating | 13343.2 | 1220 | 1236 | Power / other utility failure | Power / other utility failure-UNDER VOLT TRIP | Instrumentation | Check/ Inspect/ Test
90451122 | 2018-05-09 | A081-294XA-50200-S | 2ET-LDF-33 EHT FAULT ALM REPALCE ECM | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10243203 | 700002607282 |  | Instrumentation | 6079.07 | 150 | 182 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault- | Heat Tracing | Hardware Replacement
90451306 | 2017-09-12 | A081-2SB200N2 | FS-BA area lilghting partly OFFcondition | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10243625 | 700002373557 | ABB MALAYSIA | Electrical | 70.92 | 4 | 4 | Human Error | Human Error-Override switch in OFF | Control Circuit | Repair / correct
90451451 | 2017-10-07 | A081-2SB210N2 | 2SO210N2-33-L3-03 SOCKET OUTLET TROUBLES | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10243664 | 700002373562 | ABB MALAYSIA | Electrical | 151.79 | 16 | 16 | Loose connection | Loose connection- | Power Supply | Check/ Inspect/ Test
90451457 | 2017-09-24 | A081-2A8324 | Phase-2 DAF scrapper motor VSD alarm | MX04 | E_MOT_LV | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10243708 | 700002297890 | ABB | Electrical | 137.97 | 36 | 36 | Other - please specify in text field | Other - please specify in text field-temperature warning | Other - please specify in text field | No action
90451460 | 2017-09-30 | A081-1A8324 | TR 1 DAF SCUM BOARD PIPE SUPPORT DAMAGE | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10243710 | 700002348718 |  | Integrity | 812.51 | 11 | 29 | Fouling | Fouling-scum board was found damaged | Bolting and Gaskets | Fix / Repair
90451477 | 2017-09-13 | A081-0S8361A | SDU centrifuge A bowl motor fault | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10243721 | 700001730109 | ABB | Electrical | 0 | 4 | 0 | Overload | Overload-stall trip | Protection Relay / MCU | Adjust / reset
90451552 | 2017-09-14 | A081-1SB210N2 | 1R3021 to1R-3029 top side bulbs fused | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10243771 | 700002352082 | ABB MALAYSIA | Electrical | 40.27 | 4 | 40 | end of life | end of life- | Lamps | Check/ Inspect/ Test
90451578 | 2017-09-14 | A081-0S8361A | MSDU LIFT BEAM LOAD TEST TO CAARY OUT | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10243796 | 700001729713 |  | Rotating | 0 | 8 | 0 | Other - please specify in text field | Other - please specify in text field-lifting beam load test to be done | Other - please specify in text field | Check/ Inspect/ Test
90451989 | 2017-10-02 | A081-0S8361A | Electrical support for MSDU unit | MX04 | E_MOT_LV | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10244077 | 700001730109 | ABB | Electrical | 425.2 | 40 | 0 | end of life | end of life-Bowl bearing faulty | Motor body including fancover | Replace
90452024 | 2017-10-05 | A081-294XA-50200-S | 2ET-LPU-HD -10 EHT FAULT ALARM | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10243925 | 700002607282 |  | Instrumentation | 3415.51 | 68 | 146 | Operating at high temperature | Operating at high temperature-process temp higher than set temp | Heating element | Check/ Inspect/ Test
90452312 | 2017-11-24 | A081-0S0143B | 0S-143 B filter element replacement-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10243789 | 700002202402 | DKME | Integrity | 275.01 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90452461 | 2017-10-01 | A081-0X0104 | 0X-0104 conveyor cleaning. | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10244412 | 700002206193 |  | Electrical | 141.95 | 36 | 40 | Fouling | Fouling- | frame | Cleaned
90452602 | 2017-09-30 | A081-294XA-50200-S | 2ET-LDF-HD-01 EHT FAULT ALARM-BOTH | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10244482 | 700002607282 |  | Instrumentation | 3245.98 | 62 | 182 | Software / Hardware fault | Software / Hardware fault-thermostat faulty | Heating element | Replace
90452769 | 2017-09-29 | A081-0S0163A | 0S-163A FILTER ELEMENT REPLACEMENT-% | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10244622 | 700002200042 | DKME | Integrity | 118.66 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90453242 | 2017-10-26 | A081-0S8361A | PROCUREMENT OF ALUMINIUM BAR TO W/SHOP | MX04 |  | Routine Wrk LvL 5 | 0 |  | CENTRIFUGE | CM | ETP |  |  |  |  | 2471.31 | 0 | 0
90455645 | 2018-06-03 | A081-1F5111 | 1F5111 BURNERS CLEANING 2018-MX09 | MX09 | M_FUR_X | Routine Wrk LvL 5 | 0 |  | SMR FURNACE | CM | LPU | 10245612 | 700002348459 | KTI | Integrity | 1157.33 | 245 | 1034 | Coking | Coking-burner cleaning as per pic | Burner - cup throat | Fix / Repair | 04.10.2017 07:51:06 UTC Muthu Siva Krishnan Kalyani Rao (QRMKA2) 1F 5111 BURNERS CLEANING 2018
90455823 | 2017-10-09 | A081-1A8324 | 1A 8324 DAF scraper trip on obstacle | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10245852 | 700002348718 |  | Integrity | 397.58 | 15 | 0 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault-Proximity switch cable damaged | Proximitor | Replace
90455844 | 2018-10-08 | A081-0S8361A | MSDU DIL FLOC DRAIN VALVE T JOINT MODIFY | MX04 | M_ROT_CENT | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10245636 | 700001729713 |  | Rotating | 118.38 | 48 | 48
90456381 | 2017-11-12 | A081-0P2021 | PRCUR/FIX BROKEN FITNG OF PWR WSHR PUMP | MX09 | M_PUM_RECI | Routine Wrk LvL 5 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10245677 | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 0
90456469 | 2017-10-21 | A081-1A8324 | FFU-1 DAF SCRAPPER SCUM BOARD ROD DAMAGE | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10246449 | 700002348718 |  | Integrity | 1173.24 | 119 | 119 | Normal Wear | Normal Wear-scum board pipe damaged | Other - please specify in text field | Fix / Repair
90456490 | 2017-10-15 | A081-0S0163B | 0S-0163B filter element to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10246539 | 700002200043 | DKME | Integrity | 255.48 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90456491 | 2017-10-11 | A081-0S0143A | SCE 0S-0143A FILTER ELEMENT TO REPLACE-% | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10246538 | 700002201324 | DKME | Integrity | 488.48 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90456653 | 2017-10-30 | A081-1A8324 | FFU-1 DAF SMALL WHEEL RUBBER PEEL OFF | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10246505 | 700002348718 |  | Integrity | 470.5 | 9 | 9 | Normal Wear | Normal Wear-small wheel broken | Rotating element | Replace
90457745 | 2017-11-17 | A081-0S0163A | 0S-0163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10247736 | 700002200042 | DKME | Integrity | 4380.45 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90457746 | 2017-11-26 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10247737 | 700002200043 | DKME | Integrity | 4088.36 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90457747 | 2017-01-01 | A081-0S0123B | 0S-0123B DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10247733 | 700002200643 | DKME | Integrity | 4320.58 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90457749 | 2017-12-03 | A081-0S0123A | 0S-0123A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10247732 | 700002201322 | DKME | Integrity | 4287.81 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90457750 | 2017-12-12 | A081-0S0143A | 0S-0143A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10247734 | 700002201324 | DKME | Integrity | 3893.92 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90457751 | 2017-12-24 | A081-0S0143B | 0S-0143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10247735 | 700002202402 | DKME | Integrity | 3656.88 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90458147 | 2017-10-31 | A081-0S8361A | MSDU NOT STARTING DUE ELECTRICAL FAULT | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10248157 | 700001730109 | ABB | Electrical | 479.38 | 47 | 7 | end of life | end of life-FAN BEARING DAMAGED | Motor Starter cubicle | clean
90458258 | 2019-02-02 | A081-294XA-50200-S | TR2 FAULT ALM 2LDF-22 EHT FAULT | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10248323 | 700002607282 |  | Instrumentation | 0 | 58 | 146 | Loss of Heating | Loss of Heating- | Heat Tracing | Field repair
90458856 | 2018-01-21 | A081-2SB210N2 | BB BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10248709 | 700002373562 | ABB MALAYSIA | Electrical | 561.68 | 21 | 21 | end of life | end of life- | Lamps | Replace
90458857 | 2018-01-24 | A081-2SB210N2 | BB BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10248710 | 700002373562 | ABB MALAYSIA | Electrical | 987.73 | 39 | 29 | end of life | end of life- | Lamps | Replace
90458858 | 2018-01-21 | A081-2SB210N2 | BB BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10248711 | 700002373562 | ABB MALAYSIA | Electrical | 369.51 | 17 | 17 | end of life | end of life- | Lamps | Replace
90458865 | 2018-02-12 | A081-2SB210N2 | BB BUSTED 400W FLOODLIGHTS TO BE REPLACE | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10248718 | 700002373562 | ABB MALAYSIA | Electrical | 1165.49 | 150 | 73 | end of life | end of life- | Ballast / Ignitor / Holder | Replace
90458866 | 2018-01-21 | A081-2SB210N2 | BB BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10248719 | 700002373562 | ABB MALAYSIA | Electrical | 297.88 | 19 | 17 | end of life | end of life- | Lamps | Replace
90458867 | 2017-08-01 | A081-2SB210N2 | BB BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10248720 | 700002373562 | ABB MALAYSIA | Electrical | 414.71 | 13 | 45 | end of life | end of life- | Lamps | Replace
90458877 | 2017-12-02 | A081-2SB210N2 | BB BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10248777 | 700002373562 | ABB MALAYSIA | Electrical | 77.23 | 10 | 10 | end of life | end of life- | Lamps | Replace
90458879 | 2017-12-11 | A081-2SB200N2 | BA BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10248782 | 700002373557 | ABB MALAYSIA | Electrical | 292 | 13 | 13 | end of life | end of life- | Lamps | Replace
90458902 | 2017-12-12 | A081-2SB200N2 | BA BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10248827 | 700002373557 | ABB MALAYSIA | Electrical | 613.11 | 29 | 29 | end of life | end of life- | Lamps | Replace
90458903 | 2017-12-14 | A081-2SB200N2 | BA BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10248828 | 700002373557 | ABB MALAYSIA | Electrical | 284.87 | 12 | 48 | end of life | end of life- | Lamps | Replace
90458904 | 2017-12-10 | A081-2SB200N2 | BA BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10248829 | 700002373557 | ABB MALAYSIA | Electrical | 346.27 | 20 | 52 | end of life | end of life- | Lamps | Replace
90459065 | 2017-11-15 | A081-FIRE HYDRANT | SCE FH40 passing at 2.5 inch delivery | MX04 |  | Routine Wrk Lvl 4 | 0 |  | FIRE HYDRANT | CM | UTL | 10248602 |  |  |  | 0 | 8 | 9 |  | -Due to wear
90459066 | 2018-05-14 | A081-FIRE HYDRANT | Maintenance request for Dry-risers GTL2 | MX04 |  | Routine Wrk LvL 5 | 0 |  | FIRE HYDRANT | CM | UTL | 10248613 |  |  |  | 40.65 | 8 | 8 |  | -Drain cap missing |  |  | 31.10.2017 10:56:51 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection for GTL 2 by FIT, it was found that Dry-risers DR38, DR39, DR41 had missing drain caps. Dry-riser DR37, the rubber cap was damaged, where the chain hooks into the cap. Dry-riser DR45, the thread at the drain valve is damaged(spinning loose)See attachment for further details, location and photos of leaking dry-risers. PEFS: T4002748RevD_F001 Prioriteit: X Drawing number : See attachment for marked-up photos and Inspection report Requester Name : Leo Gaigher Phone : 55124684 07.11.2017 13:45:20 UTC Abhijit Wadekar (QRAWA8) MATERIAL NOT CODED <(>&<)> AVAILABLE FOR REPAIR / REPLACE.MAIL ATTACHED.WO PARKED UNDER WMAT.
90459116 | 2017-11-30 | A081-FIRE HYDRANT | SCE FH-133 High volume discharge seized | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10248499 |  |  |  | 0 | 0 | 6 | Other - please specify in text field | Other - please specify in text field-discharge seized cap | Other - please specify in text fields | Replace
90460027 | 2017-12-06 | A081-1SB220N2 | Lights not working at SGP Fin-fan floor | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10249498 | 700002356603 | ABB MALAYSIA | Electrical | 64.17 | 4 | 4 | end of life | end of life- | Lamps | Check/ Inspect/ Test
90460208 | 2017-11-30 | A081-0S8361A | SDU A BOWL MOTOR FAULT | MX04 | E_MOT_LV | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10249702 | 700001730109 | ABB | Electrical | 64.17 | 4 | 8 | Overload | Overload-Stall prot activatd due to pump stuckup | Other - please specify in text field | Adjust / reset
90460246 | 2017-11-15 | A081-0X0104 | 0X-104 Dr.M conveyor cover broken-OPRQ | MX04 | M_PAC_CON2 | Schedule Breaker | 0 |  | SCREW CONVEYOR | CM | FGP | 10249750 | 700002206193 |  | Electrical | 0 | 8 | 4 | Fouling | Fouling-Plugging at the end | guards/doors | Replace
90460249 | 2017-11-16 | A081-1A8324 | DAF 1 SCRAPPER SMALL WHEEL RUBBER DAMAGE | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10249679 | 700002348718 |  | Integrity | 75.75 | 0 | 0 | Other - please specify in text field | Other - please specify in text field-wheel damage | Other - please specify in text field | Replace
90460818 | 2018-12-17 | A081-FIRE HYDRANT | SCE FH40 passing at 2.5 inch delivery | MX04 |  | Routine Wrk LvL 5 | 0 |  | FIRE HYDRANT | CM | UTL | 10250117 |  |  |  | 0 | 0 | 14 |  |  |  |  | 16.11.2017 12:27:24 UTC Abhijit Wadekar (QRAWA8) Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection for GTL2 by FIT, it was found that fire hydrant FH40 was passing at the fourth 2.5 inch delivery. This is the last delivery from left to right. See attachment for further details, location and photos of passing hydrant PEFS: T4003201RevC_F001 and T4364121RevO_F001. TO ARREST THAT LEAK, TRY BY GLAND NUT TIGHTEENING BUT LEAK STILL CONTINUE. ARREST BY REPLACING CLACK WASHER. 11.11.2018 05:55:15 UTC Srinivasa Dandu (QRSDA3) Duplicate with WO 90491794
90460823 | 2017-11-28 | A081-1S0241 | 1S-0241 FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10250265 | 700002354895 | JFC CORPORATION | Integrity | 1666.15 | 16 | 50 | Product Contamination | Product Contamination- | Filter medium | Replace
90460838 | 2017-11-20 | A081-0S8361A | MSDU AIR TUBING LEAKING | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10250279 | 700001729713 |  | Rotating | 91.12 | 8 | 0 | Poor installation | Poor installation-due to fitting damaged, polytube ditech | Instrumentation | Fix / Repair
90461189 | 2017-12-12 | A081-294XA-50200-S | 2ET-LPU-051; TR2 MB EHT FAULT ALARM | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10250505 | 700002607282 |  | Instrumentation | 64.17 | 12 | 12 | Operating at high temperature | Operating at high temperature-high temp alarm | Heating element | Check/ Inspect/ Test
90461203 | 2018-04-09 | A081-FIRE HYDRANT | SCE FH332 VALVE 1 PASSING 2U0700 | MX04 |  | Routine Wrk Lvl 4 | 0 |  | FIRE HYDRANT | CM | UTL | 10250469 |  |  |  | 0 | 6 | 12 | Mechanical damage | Mechanical damage-valve seat damage | Valves | Replaced
90461206 | 2018-05-06 | A081-FIRE HYDRANT | SCE FH331 Directional handle miss-T2U700 | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10250468 |  |  |  | 61.8 | 12 | 17
90461209 | 2018-10-11 | A081-FIRE HYDRANT | SCE FH317 O/L vlv seized - T-2U0200-> | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10250466 |  |  |  | 61.81 | 6 | 12 | Fouling | Fouling-Not operated since long time | Valves | Fix / Repair
90461211 | 2018-03-10 | A081-FIRE HYDRANT | SCE FH309 LOCKING KNOB MISS NEAR 2V0511F | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10250465 |  |  |  | 163 | 6 | 4 | Other - please specify in text field | Other - please specify in text field-Thread damaged, lock knob missing | Other - please specify in text fields | Replace
90461218 | 2018-01-15 | A081-FIRE HYDRANT | SCE FH610 RELEASE KNOB MISS-SRU-3 | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10250471 |  |  |  | 50.78 | 6 | 6 | Normal Wear | Normal Wear- | Valve internals | Replace
90461448 | 2018-01-15 | A081-FIRE HYDRANT | SCE FH608 (SRU-3) BLANK CAP SEIZED | MX04 |  | Routine Wrk Lvl 4 | 0 |  | FIRE HYDRANT | CM | UTL | 10250470 |  |  |  | 0 | 6 | 6 | Other - please specify in text field | Other - please specify in text field-cap jammed because of rust formation. | Other - please specify in text field | Cleaned
90461733 | 2017-12-06 | A081-FIRE HYDRANT | SCE FH616 RELEASE KNOB MISSING | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10250472 |  |  |  | 0 | 8 | 8 | Normal Wear | Normal Wear-FH knob missing | cap | Fix / Repair
90461862 | 2017-12-05 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10250942 | 700002200043 | DKME | Integrity | 4025.02 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90461864 | 2017-01-01 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMNT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10250941 | 700002200042 | DKME | Integrity | 3869.79 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90462310 | 2017-01-01 | A081-0S0163A | 0S0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251082 | 700002200042 | DKME | Integrity | 287.7 | 0 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace
90462649 | 2017-12-13 | A081-0S8361A | RETA SDU A INTERNAL INSPECTION | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10251152 | 700001729713 |  | Rotating | 223.29 | 25 | 25 | Product Contamination | Product Contamination-Hard to rotate | Casing | Cleaned
90462778 | 2017-12-18 | A081-0S0123A | 0S-123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251422 | 700002201322 | DKME | Integrity | 3952.97 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463053 | 2017-12-20 | A081-0S0123B | 0S-123B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251599 | 700002200643 | DKME | Integrity | 3779.71 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463054 | 2017-12-20 | A081-0S0163A | 0S-163A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251600 | 700002200042 | DKME | Integrity | 3607.17 | 0 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463055 | 2017-12-20 | A081-0S0163B | 0S-0163B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251597 | 700002200043 | DKME | Integrity | 18988.03 | 24 | 44 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463056 | 2017-12-06 | A081-0S0163B | 0S-163B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251598 | 700002200043 | DKME | Integrity | 3607.17 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463057 | 2017-12-06 | A081-0S0123A | 0S-123A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251601 | 700002201322 | DKME | Integrity | 3607.17 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463061 | 2017-12-06 | A081-0S0123B | 0S-123B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251609 | 700002200643 | DKME | Integrity | 0 | 0 | 43
90463151 | 2017-12-16 | A081-1F5111 | FS-SMR1 ABC TEST TIMER NOT WORKING-> | MX04 | M_FUR_X | Routine Wrk Lvl 1 | 0 |  | SMR FURNACE | CM | LPU | 10251610 | 700002348459 | KTI | Integrity | 0 | 8 | 8 | Other - please specify in text field | Other - please specify in text field-Not configured on IPS | Other - please specify in text field | Other - please specify in text field
90463158 | 2018-01-08 | A081-1SB220N2 | AC BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10251652 | 700002356603 | ABB MALAYSIA | Electrical | 650.83 | 40 | 32 | end of life | end of life- | Lamps | Replace
90463359 | 2017-12-24 | A081-0S0123B | 0S-123B HYDROCARBON FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251718 | 700002200643 | DKME | Integrity | 1556.86 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463360 | 2017-12-09 | A081-0S0123B | 0S-0123B HC FILTER HIGH DP | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251730 | 700002200643 | DKME | Integrity | 3607.13 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463361 | 2017-12-24 | A081-0S0123A | 0S-0123A HC FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251727 | 700002201322 | DKME | Integrity | 237.61 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463363 | 2017-12-24 | A081-0S0163A | 0S-163A HYDROCARBON FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251719 | 700002200042 | DKME | Integrity | 1589.49 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463505 | 2017-12-09 | A081-0S0163A | 0S-0163A HC FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251728 | 700002200042 | DKME | Integrity | 3607.13 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463506 | 2018-04-04 | A081-0S0163B | 0S-0163B HC FILTER HIGH DP-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251729 | 700002200043 | DKME | Integrity | 5011.45 | 0 | 43
90463508 | 2017-12-10 | A081-0S0123B | 0S-123B HYDROCARBON FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251607 | 700002200643 | DKME | Integrity | 12456.26 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463752 | 2017-12-31 | A081-0S0143A | 0S-0143A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252093 | 700002201324 | DKME | Integrity | 3991.41 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463760 | 2017-12-21 | A081-0X0104 | 0X-0104 Dr M filter conveyer cleaning | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10251976 | 700002206193 |  | Electrical | 0 | 10 | 14 | Fouling | Fouling- | drive system | Cleaned
90463796 | 2018-05-24 | A081-1F5111 | HW- C12 BURNER TIP TACK WELDING | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10247261 | 700002348459 | KTI | Integrity | 1504.79 | 53 | 51 | Normal Wear | Normal Wear-Burner C-12 tack weld damaged | Burner - cup throat | Replace
90463951 | 2018-01-03 | A081-0S0123B | 0S-0123B filter element to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252309 | 700002200643 | DKME | Integrity | 99.14 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463954 | 2017-12-31 | A081-0S0123A | 0S-0123A filter element to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252308 | 700002201322 | DKME | Integrity | 218.16 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463955 | 2018-01-07 | A081-0S0143A | 0S-0143A filter element to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252310 | 700002201324 | DKME | Integrity | 3644.23 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90463956 | 2017-12-30 | A081-0S0143B | 0S-0143B FILTER ELEMENT TO BE REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252311 | 700002202402 | DKME | Integrity | 3844.11 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90464090 | 2018-01-17 | A081-0S0163A | 0S-163A filter element replacement. | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251996 | 700002200042 | DKME | Integrity | 3881.54 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90464091 | 2017-12-31 | A081-0S0123A | 0S-123A filter element replacement. | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10251978 | 700002201322 | DKME | Integrity | 7805.77 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90464239 | 2017-12-20 | A081-2SB200N2 | PRD-2SB200N2 Q16 CIRCUIT BREAKER TRIP | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10252526 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 10 | 10 | Overvoltage / undervoltage | Overvoltage / undervoltage- | Lamps | Check/ Inspect/ Test
90464308 | 2017-12-19 | A081-0S0123B | 0S-123B filter element replacement-PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252572 | 700002200643 | DKME | Integrity | 290.31 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90464309 | 2017-12-19 | A081-0S0143A | 0S-143A filter element replacement-PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252573 | 700002201324 | DKME | Integrity | 114.91 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90464615 | 2018-01-08 | A081-0S0123A | 0S-123A filter element to replaced | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252785 | 700002201322 | DKME | Integrity | 3606.94 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90464616 | 2018-01-23 | A081-0S0143A | 0S-143A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252786 | 700002201324 | DKME | Integrity | 3953.01 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90464617 | 2018-01-10 | A081-0S0143B | 0S-0143B HC filter element repalcement | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10252773 | 700002202402 | DKME | Integrity | 99.14 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90465445 | 2018-01-24 | A081-1SB210N2 | AB BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10253129 | 700002352082 | ABB MALAYSIA | Electrical | 11911.11 | 562 | 638 | end of life | end of life- | Lamps | Replace | 28.12.2017 05:00:24 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER PM WO#90446170, 90446172- ITS FOUND THAT TUBE LIGHTS FAULTY IN 1SB210N2/ CKT-01 TO CKT-09, 18WATTS - 10 PCs AND 36WATTS - 170 PCs OF TUBE LIGHTS REQUIRED. PEFS: T-4.013.384 Prioriteit: X- MOVABLE SCAFFOLDING AND A TYPE LADDER USAGE Electrical tasks: X E-isolation - Workparty X JHA needed Requester NAME : VASIM Phone : 44032804
90465494 | 2018-01-17 | A081-0S0123B | 0S-0123B FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10253445 | 700002200643 | DKME | Integrity | 1590.61 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 31.12.2017 14:43:21 UTC Balakrishna Guthu Mijar (QRBMI0) 0S-123 B Filter replacement
90465495 | 2018-01-15 | A081-0S0123B | 0S-0123B FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10253416 | 700002200643 | DKME | Integrity | 2521.14 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 31.12.2017 12:31:22 UTC Balakrishna Guthu Mijar (QRBMI0) 0S-123 B hydrocarbon need to be replacement when it gets exhausted.
90465500 | 2018-01-24 | A081-0S0143B | 0S-0143B FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10253446 | 700002202402 | DKME | Integrity | 3813.73 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 31.12.2017 14:45:00 UTC Balakrishna Guthu Mijar (QRBMI0) 0S-143 B filter replacement required
90465501 | 2018-01-15 | A081-0S0143B | 0S-0143B FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10253418 | 700002202402 | DKME | Integrity | 2134.87 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 31.12.2017 12:33:37 UTC Balakrishna Guthu Mijar (QRBMI0) 0S-143B Hydrocarbon filter need to be replaced when it gets exhausted.
90466034 | 2018-01-18 | A081-1SB210N2 | AB 1SB210N2 PANEL PHOTOCELL NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10253634 | 700002352082 | ABB MALAYSIA | Electrical | 1941.46 | 28 | 30 | end of life | end of life- | Electronic / control board | Replace | 02.01.2018 12:26:13 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 AB AREA, 1SB210N2 SWITCH BOARD PHOTOCELL NOT WORKING, NEED TO TROUBLESHOOT/ REPLACEMENT TO BE DONE. PEFS: T-4.039.718 Prioriteit: X-Scaffold required Electrical tasks: X E-isolation - Workparty X JHA needed Requester NAME : VASIM Phone : 44032804 04.01.2018 06:14:27 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 ATPRESENT DUE TO PHOTOCELL NOT WORKING, ALL AUTO LIGHTING GLOWING DURING DAY TIME ALSO, NEED TO BE RECTIFIED AT EARLIEST
90466051 | 2018-02-04 | A081-0P2021 | ERECT HOSE STORAGE YARD BELOW ALL ACC | MX09 | M_PUM_RECI | Routine Wrk LvL 5 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10253099 | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 0 |  |  |  |  | 27.12.2017 13:51:31 UTC Srinivas Bonda (QRSBO0) Clear description of the problem. TO ERECT HOSE STORAGE YARD BY SCAFFOLDING, BELOW ACC FOR ACC CLEANING AUTOMATION PROJECT. THIS HOSE STORAGE YARD TO BE ERECTED IN ALL 8 UNITS OF ASU BELOW ACC. PEFS: Prioriteit: Additional mitigations : Requester Name : srinivas bonda Phone : 44032485 26.06.2018 11:57:13 UTC Rizwan Puthalath Valiyapurayil (QRRPU3) Scaffold not required ,Confirmed with area OMC and decided to cancel work order
90466056 | 2018-02-04 | A081-0P2021 | ERECT YARD TO STORE ACC CLN SCRAP INASU5 | MX09 | M_PUM_RECI | Routine Wrk LvL 5 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10253100 | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 0 |  |  |  |  | 27.12.2017 13:57:09 UTC Srinivas Bonda (QRSBO0) Clear description of the problem. TO ERECT STORAGE YARD BY SCAFFOLDING IN ASU5 NEAR FAR09 FOR STORING SCARAP MATERIAL(HOSES, MOTORS, LADDER ETC)OF ACC CLEANING SYSTEM AFTER AUTOMATION PROJECT. PEFS: Prioriteit: Additional mitigations : Requester Name : srinivas bonda Phone : 44032485 26.06.2018 11:56:23 UTC Rizwan Puthalath Valiyapurayil (QRRPU3) Scaffold not required ,Confirmed with area OMC and decided to cancel work order
90466386 | 2018-01-16 | A081-0S0123A | 0S-0123A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10254008 | 700002201322 | DKME | Integrity | 3937.76 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 06.01.2018 22:12:06 UTC Elangovan Muthusamy (QREMU0) 0S-123A DP high filter element to be replaced.
90466387 | 2018-01-16 | A081-0S0143A | 0S-0143A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10254009 | 700002201324 | DKME | Integrity | 2037.69 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 06.01.2018 22:13:56 UTC Elangovan Muthusamy (QREMU0) 0S-143A DP high filter element to be replaced.
90467070 | 2018-01-25 | A081-0P2021 | ASU-1&6 ACC CLEANING READINESS | MX09 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10254300 | 700002199414 | PRATISSOLI | Rotating | 1415.12 | 162 | 174 |  |  |  |  | 09.01.2018 09:45:40 UTC Donald Enriquez (QRDEN0) Clear description of the problem. TO CHECK THE READINESS OF ASU8 FOR ACC CLEANING. PEFS: Prioriteit: Additional mitigations : Requester Name : DONALD Phone : 44032214 10.01.2018 04:53:20 UTC Jothikumar Manickam (QRJMA1) REQUIREMENT : Suction and discharge hoses are to be connected .suction hose from raw water line battery limit and discharge hoses are to be connected upto acc cleaning head assembly. electrical team to provide cable connection at the bottom and top . Units are ASU 6 and ASU 8. 15.01.2018 16:05:52 UTC Thameen Ansari (QRTAN0) AS PER OMC ASU-1 <(>&<)> ASU-6
90467923 | 2018-02-18 | A081-0S0143B | 0S-0143B FILTER DP HIGH,TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10255317 | 700002202402 | DKME | Integrity | 2311.06 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 17.01.2018 12:09:30 UTC Pratik Manilal Prajapati (QRPPR1) 0S-0143B Filter DP high, to be replaced
90467924 | 2018-02-18 | A081-0S0123A | 0S-0123A FILTER DP HIGH,TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10255313 | 700002201322 | DKME | Integrity | 220.24 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 17.01.2018 12:01:06 UTC Pratik Manilal Prajapati (QRPPR1) 0S-123A DP high filter element to be replaced.
90467925 | 2018-02-16 | A081-0S0143A | 0S-0143A FILTER DP HIGH,TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10255316 | 700002201324 | DKME | Integrity | 7185.41 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 17.01.2018 12:07:58 UTC Pratik Manilal Prajapati (QRPPR1) 0S-0143A Filter DP high, to be replaced
90467926 | 2018-01-22 | A081-0S0123B | 0S-0123B FILTER DP HIGH,TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10255314 | 700002200643 | DKME | Integrity | 336.12 | 24 | 43 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 17.01.2018 12:04:19 UTC Pratik Manilal Prajapati (QRPPR1) 0S-0123B DP high filter element to be replaced.
90467927 | 2018-04-11 | A081-0S0163A | 0S-0163A FILTER DP HIGH,TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10255319 | 700002200042 | DKME | Integrity | 10839.53 | 24 | 43 |  |  |  |  | 17.01.2018 12:12:34 UTC Pratik Manilal Prajapati (QRPPR1) 0S-0163A Filter DP high, to be replaced
90467928 | 2018-02-24 | A081-0S0163B | 0S-0163B FILTER DP HIGH,TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10255320 | 700002200043 | DKME | Integrity | 269.13 | 0 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 17.01.2018 12:13:51 UTC Pratik Manilal Prajapati (QRPPR1) 0S-0163B Filter DP high, to be replaced
90468558 | 2018-03-16 | A081-FIRE HYDRANT | ETU SCE FH442 Damaged manifold inlet | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10255634 |  |  |  | 2141.89 | 8 | 18 | Mechanical damage | Mechanical damage-Damaged on coupling lock | Fire water hydrant | Replace | 22.01.2018 05:07:11 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection executed by FIT, it was found that the 5 inch inlet manifold at FH442 was damaged. Maintenance can contact ER TAO Leo Gaigher for spare part. See attachment for location, further details, specifications and photos of damaged manifold. PEFS: Prioriteit: X Drawing number : T-4.094.056 and T-4.364.122 Requester Name : Leo Gaigher Phone : 55124684
90468559 | 2018-03-03 | A081-FIRE HYDRANT | SCE FH443 Missing valve/handle | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10255639 |  |  |  | 1534.44 | 6 | 6 | Material defect | Material defect-Lock screw broken and handle loosen | Valve body | Replaced | 22.01.2018 05:16:13 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection executed by FIT, it was found that the 5 inch valve/handle at FH443 was missing. See attachment for location, further details, specifications and photos of missing valve/handle. PEFS: Prioriteit: X Drawing number : T-4.094.056 and T-4.364.121 Requester Name : Leo Gaigher Phone : 55124684
90469355 | 2017-01-01 | A081-0S0123B | 0S-123B DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10256028 | 700002200643 | DKME | Integrity | 366.67 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace
90469356 | 2018-02-25 | A081-0S0123A | 0S-123A DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10256027 | 700002201322 | DKME | Integrity | 275.01 | 24 | 48 | Product Contamination | Product Contamination-replace filter element | Filter cartridges | Replace | 25.01.2018 09:47:36 UTC Elangovan Muthusamy (QREMU0) 0S-123A DP high filter element to be replaced.
90469358 | 2018-02-09 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10256137 | 700002201324 | DKME | Integrity | 12809.24 | 24 | 48 | Product Contamination | Product Contamination- | Filter medium | Replace | 25.01.2018 14:17:11 UTC Elangovan Muthusamy (QREMU0) 0S-143A DP high filter element to be replaced.
90469359 | 2018-01-24 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10256138 | 700002202402 | DKME | Integrity | 10933.29 | 0 | 48 | Product Contamination | Product Contamination- | Filter medium | Replace | 25.01.2018 14:18:06 UTC Elangovan Muthusamy (QREMU0) 0S-143B DP high filter element to be replaced.
90469389 | 2018-01-24 | A081-0P2021 | FIX ACC CLEANING BELT AND HEAD OF ASU6 | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10256205 | 700002199414 | PRATISSOLI | Rotating | 7502.67 | 88 | 132 | Product Contamination | Product Contamination- | Other - please specify in text field | Cleaned | 26.01.2018 10:17:31 UTC Donald Enriquez (QRDEN0) Clear description of the problem. TO FIX THE ACC CLEANING BELT AND HEAD OF ASU6 AND TO SUPPORT DURING TRIAL RUN. PEFS: Prioriteit: Additional mitigations : Requester Name : Donald Phone : 44032213
90469390 | 2018-01-27 | A081-0P2021 | SUPPORT ASU6 ACC CLEANING TRIAL RUN | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10256206 | 700002199414 | PRATISSOLI | Rotating | 963.16 | 32 | 0 | Other - please specify in text field | Other - please specify in text field-During start | Other - please specify in text field | Fix / Repair | 26.01.2018 10:23:09 UTC Donald Enriquez (QRDEN0) Clear description of the problem. TO SUPPORT THE ASU6 ACC CLEANING DURING TRIAL RUN. PEFS: Prioriteit: Additional mitigations : Requester Name : DONALD Phone : 44032213 01.02.2018 13:13:03 UTC Mutharasu Subbaih (QRMSU8) Cleaning System was starter found normal
90469470 | 2018-02-12 | A081-0S0143A | 0S-143A filter element replacement. | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10256226 | 700002201324 | DKME | Integrity | 0 | 24 | 48 | Product Contamination | Product Contamination- | Filter medium | Replace | 27.01.2018 05:48:40 UTC Dasarathi Bisoyi (QRDBI0) Observed high DP across 0S-0143A. Need to replace the filter elements.
90469613 | 2018-04-12 | A081-1SB220N2 | AC BUSTED TUBELIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10256345 | 700002356603 | ABB MALAYSIA | Electrical | 991.3 | 29 | 17 | end of life | end of life- | Lamps |  | 28.01.2018 12:17:22 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER HOG PROJECT TEAM INSPECTION, IT WAS FOUND THAT TUBE LIGHTS FAULTY NEAR 1K-1122 AND 1K-1112 AREA, NEED TO BE REPLACED, 36WATTS TUBELIGHT- 20 PCS REQUIRED. PEFS: T-4.013.134 / T-4.013.137 Prioriteit: X- 'A' TYPE LADDER USAGE Electrical tasks: X E-isolation - Workparty X JHA needed Requester NAME : WISNU Phone : 44032804 08.03.2018 07:31:00 UTC Mohammad Alam (QRMANR) ETA IS 30/04/2018
90469614 | 2018-02-03 | A081-0X0104 | 0X-104 screw conveyor cleaning | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10256359 | 700002206193 |  | Electrical | 0 | 10 | 14 | Other - please specify in text field | Other - please specify in text field-moisture | Other - please specify in text field | Cleaned | 28.01.2018 20:48:39 UTC Elangovan Muthusamy (QREMU0) 0X-0104 screw conveyor to be cleaned for DrM filter next batch preparation.
90469671 | 2018-01-30 | A081-0P2021 | PROVIDE OPS SUPPORT ACC CLEANING ASU6 | MX09 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10256436 | 700002199414 | PRATISSOLI | Rotating | 0 | 18 | 18 | Blocked filters | Blocked filters- | Other - please specify in text field | Cleaned | 29.01.2018 10:32:23 UTC Kannan Perumal (QRKPE0) Clear description of the problem. TO PROVIDE OPERATION ASSISTANT FOR ASU-6 ACC CLEANING. PEFS: Prioriteit: Additional mitigations : Requester Name : KANNAN PERUMAL Phone : 44032213 29.01.2018 12:08:13 UTC Srinivas Bonda (QRSBO0) TO DO FIRE WATER CLEANING OF ACC FIN FANS
90469903 | 2018-10-22 | A081-1SB210N2 | AB LIGHT DIFFUSER DAMAGED TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10256372 | 700002352082 | ABB MALAYSIA | Electrical | 972.8 | 16 | 16 | Mechanical damage | Mechanical damage- | Lamps |  | 29.01.2018 05:01:33 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AB AREA, 1LFN210N204L305, 1LFN210N204L203 36WATTS TUBE LIGHT FITTIG DIFFUSERS FOUND DAMAGED AND LAMPS ALSO TO BE REPLACED WITH NEW. PEFS: T-4.013.089 Prioriteit: X- 'A' TYPE LADDER USAGE Electrical tasks: X E-isolation - Workparty X JHA needed Requester NAME : VASIM Phone : 44032804 11.02.2018 11:58:34 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 WE FOUND 1LFN210N212L203 - 36W LIGHT FITTING DIFFUSER DAMAGE, INCLUDE THIS IN ADDITION TO THE ABOVE. 08.03.2018 06:54:17 UTC Mohammad Alam (QRMANR) AS OF TODAY ETA IS 20/04/2018
90469938 | 2018-02-17 | A081-0P2021 | PROVIDE ELECT'L SUPPORT FOR ACC CLEANING | MX09 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10256128 | 700002199414 | PRATISSOLI | Rotating | 3174.1 | 562 | 624 |  |  |  |  | 25.01.2018 12:27:40 UTC Donald Enriquez (QRDEN0) Clear description of the problem. TO PROVIDE ELECTRICAL SUPPORT FOR ACC CLEANING OF ASU1 TO 8 AS PER OPERATION PRIORITY PEFS: Prioriteit: Additional mitigations : Requester Name : Donald Phone : 44032213
90470194 | 2018-02-07 | A081-0S8361A | MSDU CENTRIFUGE ELECTRCAL FAULT | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10256726 | 700001730109 | ABB | Electrical | 524.98 | 54 | 24 | Ingress of water / condensation | Ingress of water / condensation-due to sludge accumulation | RTD / Thermister / Leakage Sensors | clean | 31.01.2018 14:25:40 UTC Raju Sutham (QRRSU3) Clear description of the problem. ETP MSDU Electrical fault appeared during start up. please rectify PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : Raju.s Phone : 44032215 05.02.2018 08:23:06 UTC V. Velyogeeswaran (QRVVE2) Phone 4403 2795 fault appeared in HMI as mentioned below,need instrument support also to check 7 rectify the fault 067-DEFAULT ELECTRIC OF POLYMER PUMP M-203 104-DEFAULT TEMPERATURE POLYMER PUMP TOO HIGH 095-DEFAULT LEVEL TOO LOW PURE POLYMER TANK 12.02.2018 03:23:38 UTC V. Velyogeeswaran (QRVVE2) Phone 4403 2795 found the level transmitter in the centrifuge got choked,cleaned well, trial taken ,centrifuge tripped on overload,then informed to mech to clean the centrifuge accumulated sludge..
90470442 | 2018-02-05 | A081-1A8324 | DAF1 scraper support broken | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10256918 | 700002348718 |  | Integrity | 787.75 | 0 | 0 | Mechanical damage | Mechanical damage-Scum board L pipe was damaged | Supports | Fix / Repair | 03.02.2018 06:12:46 UTC "Astronomo, " Edgardo (QREAS0) Clear description of the problem. DAF scraper TR1 1A 8324 support pipe welding joint found damaged/broken. To be attended. PEFS: Prioriteit: Electrical tasks: X E-isolation Requester Name : EDGARDO Phone : 44032215 07.02.2018 06:59:02 UTC Rajeshwar Prasad (QRRPR1) Phone 33003359 DAF scum board removed and sent to work shop for welding and repair, shifted back to site and fixed back to position. During fixing tech found one more u clamp loosened and fixed it back. test run done, job completed.
90470729 | 2018-04-12 | A081-0P2021 | LEAK WAT PG HOSE PINHOLE ACC CLEAN PUMP | MX04 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10257017 | 700002199414 | PRATISSOLI | Rotating | 157.11 | 12 | 12 | Normal Wear | Normal Wear-Need to change the impulse tubing for pa | Instrumentation | Replace | 04.02.2018 11:49:04 UTC Mohamed Yunus (QRMLI1) Clear description of the problem. ACC CLEANING PUMP0P-2092 LOCATED AT ASU1 HAVING FOLLOWING ISSUES. 1.SUCTION PG HOSE AT PUMP ASSEMBLY PIN HOLE LEAK. 2.DISCHARGE PG HOSE AT PUMP ASSEMBLY NOT HEALTHY. PEFS: Prioriteit: Additional mitigations : X JHA needed Requester Name : Yunus Phone : 44032213
90470949 | 2018-02-07 | A081-0P2021 | ASU6 ACC Cleaning skid motor not working | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10257230 | 700002199414 | PRATISSOLI | Rotating | 282.83 | 32 | 8 | Adverse Weather Conditions | Adverse Weather Conditions-Emerg stop button strip broken | Other - please specify in text field | Replace | 06.02.2018 08:11:57 UTC Bala Subramanian (QRBSU0) Clear description of the problem. ASU6 ACC CLEANING SKID NOZZLE DRIVE MOTOR NOT WORKING PEFS: Prioriteit: Requester Name : BALASUBRAMANIAN Phone : 2213 12.02.2018 04:21:39 UTC John Babate (QRJBA6) Remote control button wire strip broken to cause emerg stop always open. X4:5 terminal for emer circuit found loose connection-retightned. Up and down limits switches checked and found working.
90471111 | 2018-02-11 | A081-0S0123B | 0S-0123B HIGH DP | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257399 | 700002200643 | DKME | Integrity | 0 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 10:13:11 UTC Sudhakaran Ravindran (QRSRAA) 0S-123B filter element need to be replace
90471112 | 2018-02-09 | A081-0S0123A | 0S-0123A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257397 | 700002201322 | DKME | Integrity | 0 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 10:07:05 UTC Sudhakaran Ravindran (QRSRAA) 0S-0123A filter tobe replaced.
90471113 | 2018-04-13 | A081-0S0123A | 0S-0123A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257396 | 700002201322 | DKME | Integrity | 3623.3 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 10:06:03 UTC Sudhakaran Ravindran (QRSRAA) 0S-0123A DP HIGH,Filter element to be replaced.
90471114 | 2018-02-13 | A081-0S0123B | 0S-0123B DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257393 | 700002200643 | DKME | Integrity | 0 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 09:59:19 UTC Sudhakaran Ravindran (QRSRAA) 0S-0123A Filter element to be replaced.
90471115 | 2018-03-30 | A081-0S0143A | 0S-0143A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257395 | 700002201324 | DKME | Integrity | 3607.5 | 35 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 10:05:00 UTC Sudhakaran Ravindran (QRSRAA) 0S-0123A filter to be replaced. 07.02.2018 11:02:35 UTC George John (QRGJO1) 0S-0143A filter to be replace
90471117 | 2018-03-30 | A081-0S0163A | 0S-0163A FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257415 | 700002200042 | DKME | Integrity | 3640.28 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 11:21:25 UTC Edwin Reyes (QRERE0) 0S-0163A FILTER REPLACE
90471118 | 2018-04-12 | A081-0S0163B | 0S-0163B FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257414 | 700002200043 | DKME | Integrity | 3798.32 | 20 | 28 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 11:20:16 UTC Edwin Reyes (QRERE0) 0S-0163B FILTER REPLACE
90471119 | 2018-04-11 | A081-0S0143A | 0S-0143A FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257413 | 700002201324 | DKME | Integrity | 3734.2 | 9 | 28 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 11:19:58 UTC Edwin Reyes (QRERE0) 0S-0143a FILTER REPLACE
90471120 | 2018-08-06 | A081-0S0143A | 0S-0143A FILTER REPLACE-> | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257407 | 700002201324 | DKME | Integrity | 3684.57 | 9 | 28 |  |  |  |  | 07.02.2018 11:13:49 UTC Edwin Reyes (QRERE0) 0S-0143A FILTER REPLACE
90471121 | 2018-02-11 | A081-0S0143B | 0S-0143B FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257412 | 700002202402 | DKME | Integrity | 0 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 11:18:26 UTC Edwin Reyes (QRERE0) 0S-0143B FILTER REPLACE
90471122 | 2018-03-06 | A081-0S0143B | 0S-0143B FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257409 | 700002202402 | DKME | Integrity | 488.09 | 35 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 11:16:37 UTC Edwin Reyes (QRERE0) 0S-0143B FILTER REPLACE
90471123 | 2018-04-26 | A081-0S0143B | 0S-0143B FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257408 | 700002202402 | DKME | Integrity | 3539.19 | 9 | 28 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 11:16:12 UTC Edwin Reyes (QRERE0) 0S-0143B FILTER REPLACE
90471124 | 2018-06-11 | A081-0S0123B | 0S-0123B FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257420 | 700002200643 | DKME | Integrity | 4083.87 | 9 | 28 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 11:30:55 UTC Edwin Reyes (QRERE0) 0S-0123B FILTER REPLACE
90471125 | 2018-04-12 | A081-0S0123B | 0S-0123B FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257422 | 700002200643 | DKME | Integrity | 3603.87 | 24 | 43 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 11:32:00 UTC Edwin Reyes (QRERE0) 0S-0123B FILTER REPLACE
90471126 | 2019-01-20 | A081-0S0123A | 0S-0123A FILTER REPLACE-> | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257419 | 700002201322 | DKME | Integrity | 3692.15 | 24 | 43 |  |  |  |  | 07.02.2018 11:30:21 UTC Edwin Reyes (QRERE0) 0S-0123A FILTER REPLACE
90471127 | 2018-05-20 | A081-0S0123A | 0S-0123A FILTER REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10257417 | 700002201322 | DKME | Integrity | 5073.51 | 24 | 28 | Product Contamination | Product Contamination- | Filter medium | Replace | 07.02.2018 11:29:10 UTC Edwin Reyes (QRERE0) 0S-0123A FILTER REPLACE
90471572 | 2018-02-17 | A081-0X0104 | 0X-104 CONVEYER NEED TO BE CLEANED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10257627 | 700002206193 |  | Electrical | 227.72 | 14 | 14 | Product Contamination | Product Contamination-Due to moisture | rollers | Cleaned | 10.02.2018 10:03:29 UTC Dasarathi Bisoyi (QRDBI0) Clear description of the problem. Screw Conveyer (0X0104) need to cleaned for next Dr M filter batch preparation. PEFS: Prioriteit: Electrical tasks: X E-isolation Requester Name : Dasarathi Bisoyi Phone : 44032115
90471623 | 2018-04-01 | A081-1F5111 | HW-1F5111 OBSERVATN WINDOW RED HOTDCON** | MX04 | M_FUR_X | Routine Wrk Lvl 2 | 0 |  | SMR FURNACE | CM | LPU | 10257027 | 700002348459 | KTI | Integrity | 21473.52 | 77 | 488 | Material defect | Material defect- | Casing | Replace | 04.02.2018 13:24:50 UTC Paulraja Mathavadian (QRPMA1) Clear description of the problem. 1F-5111 observation windows red hot to be rectified.(Raised as per OMC) PEFS: Prioriteit: Additional mitigations : Requester Name : Paulraja Mathavadian Phone : 44032414 17.12.2019 06:50:08 UTC R. Thridappilly Gopalakrishnan (QRRTH2) MOC: P-5100-2521
90471704 | 2018-03-10 | A081-2SB210N2 | 2R-3011A/B 2nd Flr Floodlight notworking | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10257768 | 700002373562 | ABB MALAYSIA | Electrical | 72.92 | 4 | 4 | end of life | end of life- | Lamps | Other - please specify in text field | 11.02.2018 12:15:40 UTC Chon Sung Ong (QRCON0) Clear description of the problem. 2R-3011/12 A/B. Second floor (Inlet valve platform) All Flood light not working. PEFS: Prioriteit: Additional mitigations : X Scaffold Requester Name : Ong Chon Sung Phone : 14.02.2018 05:13:36 UTC Mageshkumar Rajaram (QRMRA1) Phone 44032804 2804 Functional location changed.
90471984 | 2018-03-27 | A081-0S8361A | MSDU PACKAGE PARKING TO BE ADJUSTED | MX09 | M_ROT_CENT | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10253021 | 700001729713 |  | Rotating | 21702.4 | 652 | 369 |  |  |  |  | 26.12.2017 08:16:00 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. MSDU package parking to be adjusted for new MSDU unit place. Piping, hoses, electric cables and instrument air tubing also adjusted. Scaffolding starirs to be adjusted also PEFS: Prioriteit: Additional mitigations : X WPS/ Work instruction needed X Scaffold X Crane Crane needed to shifted the package Electrical tasks: Requester Name : Bagus Phone : 44032215 15.02.2018 09:31:46 UTC Siby George (QRSGE0) 4X70sq mm cable required; 250m.
90472205 | 2018-03-07 | A081-0S8361A | RETA MSDU PRODUCT CONVEYORS BROKEN | MX04 | M_ROT_CENT | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10257569 | 700001729713 |  | Rotating | 687.87 | 210 | 312 | Operating outside design | Operating outside design-Conveyor shaft damaged | Shaft | Fix / Repair | 09.02.2018 03:38:08 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. MSDU product conveyor M401A and M401B screw conveyor broken in the middle. dry sludge accumulation on the bellow PEFS: MSDU PEFS Prioriteit: Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-Disconnect X E-isolation Requester Name : Bagus Phone : 44032215 14.04.2018 04:55:01 UTC Rajeshwar Prasad (QRRPR1) Phone 33003359 Damged conveyor repaired and fixed it, MSDU unit shifted from one location to another locatoin all hose connection inlet and out let done. One PVC joint found damged also repaired it and fixed it. Job completed, handed over to ops, taken in service, job completed.
90472372 | 2018-03-01 | A081-0P2021 | LEAK WAT PR TAPPING PT 0P-2021 | MX04 | M_PUM_RECI | Routine Wrk Lvl 2 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10257435 | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 0 |  |  |  |  | 07.02.2018 13:19:08 UTC Jose Jr Vinluan (QRJVI1) Clear description of the problem. ACC cleaning pump 0P-2021 discharge pressure transmitter topping point is leaking. Check and rectify PEFS: Prioriteit: Additional mitigations : Requester Name : Lelono Phone : 2214 25.02.2018 06:01:57 UTC Shabbir Barwaniwala (QRSBA9) DUPLICATE OF WO# 90470729
90472842 | 2018-03-07 | A081-0S8361A | SDU A CENTRI DISCH BELLOW DAMAGED | MX04 |  | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10257996 |  |  |  | 2978.51 | 26 | 33 |  |  |  |  | 13.02.2018 10:14:03 UTC Eric Ates (QREAT0) Clear description of the problem. SDU B CENTRIFUGE DISCHARGE CHUTE BELLOW FOUND DAMAGED,SOME PORTION ALREADY PARTIALY OPEN.NEEDS TO BE REPLACED. PEFS: T-4.253.274 Prioriteit: Additional mitigations : X WPS/ Work instruction needed Requester Name : ERIC ATES Phone : 44032215 12.03.2018 14:19:33 UTC Subash Rajendran (QRSRAP) AS REQUESTED BY OMC FLOC CHANGED FROM 'B' TO 'A'
90476144 | 2018-03-17 | A081-294XA-50200-S | 2CP400X7 ELECT TRACING FAIL ON ENMC** | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10258929 | 700002607282 |  | Instrumentation | 0 | 13 | 13 | Overvoltage / undervoltage | Overvoltage / undervoltage- | Heating element | Check/ Inspect/ Test | 25.02.2018 01:32:53 UTC Ruminkumar Patel (QRRPA6) Clear description of the problem. 2CP400X7 ELECT TRACING FAIL ON ENMC ELECT TRACING CMN FAULT ALARM ON DCS, SB SAP RAISED ON ELECT REQUEST. PEFS: Prioriteit: Additional mitigations : Requester Name : RUMIN Phone : 2413 17.03.2018 11:46:39 UTC Sivaramakrishnan Krishnapandi (QRSKR4) found the circuit Q12 was tripped condition in 2SB400E05,so checked the all circuits and IR value taken.the value was more than 20 giga ohms.then resetted the circuit.now its working normal.
90479162 | 2018-08-07 | A081-FIRE HYDRANT | SCE FH142 in ETP cam lug missing | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10259048 |  |  |  | 150.73 | 6 | 6 | Other - please specify in text field | Other - please specify in text field-CAM LUG MISSING | Other - please specify in text field | Other - please specify in text field | 26.02.2018 10:59:31 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the planned Tier 1 drill in ETP on the 25th of February 2018, it was found that the winged cam lug from fire hydrant FH142 was missing. The hydrant location is in ETP Road E-3 on the North side of Analyzer House 13. Due to the lug being missing, the blank cap in the 2.5 inch delivery is seized. See attachment for details of fire hydrant. PEFS: Prioriteit: Additional mitigations : Requester Name : Leo Gaigher Phone : 55124684 31.08.2018 01:10:45 UTC SREENIVASA LAKKARAJU (QRSLA4) FIXED THE CLAMP FOR HYDERDENT ,JOB COMPLETED
90479166 | 2018-04-11 | A081-0S0143B | 0S-0143B FILTER ELEMENTS TO BE REPLACED- | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10259759 | 700002202402 | DKME | Integrity | 22639.47 | 9 | 28 |  |  |  |  | 06.03.2018 12:18:37 UTC Dasarathi Bisoyi (QRDBI0) Observed high DP across 0S-0143B. Needs to replace the filter elements.
90479281 | 2018-03-22 | A081-0S8361A | MSDU temporary heater lying on the floor | MX04 | E_MOT_LV | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10259888 | 700001730109 | ABB | Electrical | 28.52 | 6 | 6 | Mechanical damage | Mechanical damage-due to corrosion | Space heater | Check/ Inspect/ Test | 08.03.2018 02:06:47 UTC Raju Sutham (QRRSU3) Clear description of the problem. ONE OF THE temporary room heater in MSDU centrifuge cable with heater ON and very hot and laying on floor dangerously. The connecting wires from main supply is also very unsafe condition. Tomorrow people will work in MSDU near that Hot Heater. We were not able to find any isolation switch for this. Please switch off the heater and to be fixed safely. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : Raju.s Phone : 44032215 02.04.2018 13:17:08 UTC V. Velyogeeswaran (QRVVE2) Phone 4403 2795 heater already damaged condition,so isolation done <(>&<)> remove the cable from heater.
90479979 | 2018-03-28 | A081-1SB220N2 | 1LFN220N201L220 DIFFUSER DAMAGED | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10259250 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 2 | 2 | end of life | end of life- | Casing / enclosure | Replace | 28.02.2018 07:09:28 UTC Mageshkumar Rajaram (QRMRA1) Phone 44032804 2804 Clear description of the problem. LIGHT FIXTURE (36W) DIFFUSER MORE DAMAGED, NEED TO REPLACE. SCAFFOLDING NOT REQUIRED BEHIND 1SS220 SUBSTATION PEFS: Prioriteit: Electrical tasks: X E-Disconnect X JHA needed Requester Name : MAGESHKUMAR RAJARAM Phone : 31548616 01.03.2018 04:51:50 UTC Mageshkumar Rajaram (QRMRA1) Phone 44032804 2804 Need to fix the diffuser before startup
90480390 | 2018-04-14 | A081-0P2021 | PROCURE LONG BELTS FOR ACC CLEANING PUMP | MX09 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10260912 | 700002199414 | PRATISSOLI | Rotating | 2121.69 | 0 | 1 |  |  |  |  | 14.03.2018 12:26:53 UTC Ahmed Maqsood (QRAMA4) Clear description of the problem. PROCURE LONG BELTS FOR ACC CLEANING PUMP 0P-2021 PEFS: Prioriteit: Additional mitigations : Requester Name : MAQSOOD AHMED Phone : 309744337
90481185 | 2018-03-21 | A081-0X0104 | 0X-0104 is not available-OPLN | MX04 | M_PAC_CON2 | Schedule Breaker | 0 |  | SCREW CONVEYOR | CM | FGP | 10261390 | 700002206193 |  | Electrical | 0 | 8 | 18 | Fouling | Fouling-Fouling by celulose | guards/doors | Cleaned | 21.03.2018 05:30:55 UTC Dasarathi Bisoyi (QRDBI0) DEFECT FOUND: 0X-0104 is not available. Checked by electrical person and observed internal trip. Suspected mechanical stuck issue in screw conveyer. EQUIPMENT FUNCTION: Cellulose extruder SUGGESTED FIX REQUIRED: Need to check the issue by both mechanical and electrical team. MANNING, MATERIAL AND TOOLS REQUIRED: Electrical/ mechanical Team. LOCATION/ACCESS ISSUES: No access issue. HEALTH, SAFETY <(>&<)> ENVIRONMENTAL CONSIDERATIONS: slip, trip, heat stress. REASONING BEHIND CMPT RANKING: 1B.
90481247 | 2018-09-23 | A081-2SB200N2 | BA BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10261286 | 700002373557 | ABB MALAYSIA | Electrical | 1288.13 | 54 | 115 | end of life | end of life- | Lamps | Replace | 19.03.2018 17:38:41 UTC Venkata Rachakonda (QRVRA0) Clear description of the problem. BA AREA FLUORESCENT BUSTED BULBS TO BE REPLACED PEFS: Prioriteit: Additional mitigations : Requester Name : SUBBU Phone : 44032311 21.03.2018 12:29:16 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 CORRECT EQUIPMENT CODE CHANGED TO 2SB200N2 BB AREA, BUSTED TUBE LIGHTS TO BE REPLACED FOR ENCLOSED AREA, 36WATTS TUBELIGHTS - 60 PCs REQUIRED. X-Scaffold required - MOVABLE TYPE/ A TYPE LADDER Electrical tasks: X E-isolation - Workparty X JHA needed 31.03.2018 07:38:50 UTC Mohammad Alam (QRMANR) AS OF TODAY ETA IS 30/05/2018
90481251 | 2018-05-02 | A081-2SB210N2 | BB BUSTED TUBE LIGHTS TO BE REPLACED | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10261290 | 700002373562 | ABB MALAYSIA | Electrical | 2234.16 | 3 | 110 |  |  |  |  | 19.03.2018 17:51:50 UTC Venkata Rachakonda (QRVRA0) BB BUSTED FLUORESCENT BULBS TO BE REPLACED 21.03.2018 12:14:36 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 CORRECT EQUIPMENT CODE CHANGED TO 2SB210N2 Clear description of the problem. BB AREA, BUSTED TUBE LIGHTS TO BE REPLACED FOR ENCLOSED AREA, 36WATTS TUBELIGHTS - 80 PCs REQUIRED. PEFS:- Prioriteit: X-Scaffold required - MOVABLE TYPE/ A TYPE LADDER Electrical tasks: X E-isolation - Workparty X JHA needed Requester NAME : PRABAKARAN Phone : 44032804 27.03.2018 12:46:42 UTC Mohammad Alam (QRMANR)
90481635 | 2018-04-11 | A081-294XA-50200-S | 2ET-LPU-080 EHT FAULT;C/O TO REDUNDANT * | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10261634 | 700002607282 |  | Instrumentation | 4135.47 | 108 | 140 | Design Error | Design Error- | Primary Sensor | Hardware Replacement | 25.03.2018 01:01:26 UTC Manik Kalita (QRMKA4) Phone 33695751 Clear description of the problem. 294XA50400 COMMON FAULT ALARM GENERATED DUE TO 2ET-LPU-080(2SW7402411) EHT FAULT,SWITCH CHANGE OVER FORM REDINDENT TO MAIN,NOW NO MORE ALARM ,RECTIFICATION REQUIRE. EHT GOING TO 2V-4701 RV, CDW RX STRUCTURE TOP PLATFORM PEFS: T-4.101.199 Prioriteit: Additional mitigations : X Scaffold X Insulation Electrical tasks: X E-Disconnect X JHA needed Requester Name : MANIK KALITA Phone : 44032413
90481640 | 2018-04-02 | A081-0X0104 | 0X-104 conveyor cleaning | MX09 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10261565 | 700002206193 |  | Electrical | 0 | 8 | 14 | Other - please specify in text field | Other - please specify in text field-Screw conveyor getting choked | Other - please specify in text field | Cleaned | 23.03.2018 01:53:09 UTC Elangovan Muthusamy (QREMU0) 0X-104 conveyor to be cleaned for DrM filter batch preparation
90482381 | 2019-06-02 | A081-0P2021 | LEAK ACC CLEANING PUMP SUC & RECY HOSE** | MX04 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10261773 | 700002199414 | PRATISSOLI | Rotating | 8086.63 | 50 | 50 | Normal Wear | Normal Wear- | Other - please specify in text field | Replace | 26.03.2018 12:24:12 UTC Thameen Ansari (QRTAN0) THIS NOTIFICATION RAISED WITH REFERENCE TO WO 90470728 04.02.2018 11:45:53 UTC Mohamed Yunus (QRMLI1) Clear description of the problem. ACC CLEANING PUMP 0P-2021 LOCATED AT ASU1 HAVE FOLLOWING ISSUES. 1. SUCTION HOUSE PINEHOLE LEAK 2. RECYCLE HOSE AT PUMP ASSEMBLY HAS LEAK. PEFS: T-4.133.667 Prioriteit: Additional mitigations : X JHA needed Requester Name : Yunus Phone : 44032213 22.05.2018 07:19:01 UTC Thameen Ansari (QRTAN0) WAITING FOR MATERIAL CODIFICATION. 31.07.2018 06:05:36 UTC Thameen Ansari (QRTAN0) WAITING FOR MATERIAL. 11.07.2019 11:11:36 UTC Weston Thampy (QRWTH0) Remove old hoses and installed new hoses on site .
90482896 | 2018-03-28 | A081-0P2021 | ASU-6 RUPTURED DISCH LINE 0P-2021(WELD) | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10261815 | 700002199414 | PRATISSOLI | Rotating | 836.98 | 74 | 177 |  |  |  |  | 27.03.2018 01:07:12 UTC Glen Camacho (QRGCA0) Clear description of the problem. RAPTURED DISCHARGE LINE OF ACC CLEANING PUMP 0P-2021 IN ASU6 PEFS: Prioriteit: Additional mitigations : Requester Name : GLEN Phone : 2214
90483588 | 2018-04-15 | A081-0S0163A | 0S-163 A HC filter replacement | MX04 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10262106 | 700002200042 | DKME | Integrity | 0 | 0 | 0 |  |  |  |  | 30.03.2018 11:40:55 UTC Rajesh Choudhari (QRRCH2) 0S-163 A string-3 hydro carbon filter is in choked condition, need to replace filter cartridges. 19.04.2018 10:16:32 UTC Shynesh Chaladan (QRSCHC) WO wrongly created in MX-04. Hence cancelled as instructed by OMC
90483590 | 2018-11-13 | A081-0S0143A | 0S-143A HC FILTER REPLACEMENT-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10262107 | 700002201324 | DKME | Integrity | 5593.6 | 29 | 48 | Product Contamination | Product Contamination- | Filter medium | Replace | 30.03.2018 11:43:32 UTC Rajesh Choudhari (QRRCH2) 0S-143 A String-2 HC filter cartridges need to replace.
90485958 | 2018-04-29 | A081-1F5111 | 1F5111 BURNNER CLEANING; MAY2018 | MX09 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10263474 | 700002348459 | KTI | Integrity | 26506.87 | 677 | 968 | Product Contamination | Product Contamination-Combustion deposit | Burner - cup throat | Fix / Repair | 11.04.2018 23:27:55 UTC Darwin Montanez (QRDMO1) Clear description of the problem. 1F-5111 burner cleaning required as per Technologist's advice. PEFS: T-13.370.743 Prioriteit: Requester Name : Darwin Montanez Phone : 55786794 27.05.2018 10:21:44 UTC Sivakumar Dhandapani (QRSDH1) TOTAL 10 BURNERS CLEANED. AS DISCUSSED IN DAILY MEETING, OMCE HAS CONFIRMED TO CLOSE THE WO.
90486082 | 2018-04-20 | A081-0S0163A | 0S-0163A HC FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10263540 | 700002200042 | DKME | Integrity | 239.75 | 29 | 48 | Product Contamination | Product Contamination- | Filter medium | Replace | 12.04.2018 12:09:51 UTC Sivakumar Manokaran (QRSMAA) 0s-0163A HC filter element choke need to repalce the filter element.
90486083 | 2018-05-12 | A081-0S0163B | 0S-0163B HC FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10263541 | 700002200043 | DKME | Integrity | 1481.42 | 0 | 48 |  |  |  |  | 12.04.2018 12:12:01 UTC Sivakumar Manokaran (QRSMAA) 0s-0163B HC filter element need to repalcement.
90486084 | 2018-05-29 | A081-0S0123B | 0S-0123B HC FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10263543 | 700002200643 | DKME | Integrity | 1438.24 | 0 | 48 |  |  |  |  | 12.04.2018 12:15:48 UTC Sivakumar Manokaran (QRSMAA) 0s-0123B HC filter element choke need to replace the filter element.
90486085 | 2018-12-03 | A081-0S0123A | 0S-0123A HC FILTER ELEMENT REPLACEMENT-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10263542 | 700002201322 | DKME | Integrity | 307.85 | 29 | 48 |  |  |  |  | 12.04.2018 12:13:46 UTC Sivakumar Manokaran (QRSMAA) 0s-0123A HC filter choke need to replace the filter element.
90486086 | 2018-05-02 | A081-0S0143B | 0S-0143B HC FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10263538 | 700002202402 | DKME | Integrity | 3692.54 | 29 | 48 | Product Contamination | Product Contamination- | Filter medium | Replace | 12.04.2018 12:01:30 UTC Sivakumar Manokaran (QRSMAA) 0S-0143B HC filter element choke need to be repalced
90486174 | 2018-04-23 | A081-1A8324 | Train-1 DAR scum board support rod damag | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10263650 | 700002348718 |  | Integrity | 1284.7 | 115 | 127 |  |  |  |  | 14.04.2018 10:46:47 UTC Raju Sutham (QRRSU3) Clear description of the problem. TRAIN-1 DAF SCUM BOARD SUPPORT ROD WELDING JOINT BROKEN CONDITION, NEED TO ATTEND PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. IMPROPER SKIMMING OF DAF Additional mitigations : Electrical tasks: X E-isolation Requester Name : Raju.s Phone : 44032215 15.04.2018 07:26:38 UTC Frank Faroj (QRFFA0) PHOTO ATTAHCED TO THIS NOTIFIATION.
90486342 | 2018-04-18 | A081-0X0104 | 0X-104 conveyor cleaning | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10263714 | 700002206193 |  | Electrical | 0 | 10 | 14 | Fouling | Fouling- | drive system | Check/ Inspect/ Test | 15.04.2018 10:28:26 UTC Elangovan Muthusamy (QREMU0) 0X-104 conveyor cleaning to be cleaned for next batch preparation.
90486929 | 2018-05-17 | A081-0S0163A | 0S-163 A filter element need to replace. | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10264061 | 700002200042 | DKME | Integrity | 1732.13 | 29 | 53 | Product Contamination | Product Contamination- | Filter medium | Replace | 18.04.2018 11:30:54 UTC Dasarathi Bisoyi (QRDBI0) Observed high DP across 0S-0163A. Need to replace teh filter elements.
90486931 | 2018-04-29 | A081-0S8361A | MSDU AUTO GREASER NEED TO BE REPLACED | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10264071 | 700001729713 |  | Rotating | 29.11 | 4 | 4 |  | - | Lubricator |  | 18.04.2018 12:03:59 UTC Leo Miranda (QRLMI0) Clear description of the problem. MSDU CENTRIFUGE AUTO GREASER NEED TO BE REPLACED WITH NEW ONE. PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. UNABLE TO KEEP THE CENTRIFUGE IN SERVICE WITHOUT AUTO GREASER. Additional mitigations : Requester Name : LEO Phone : 44032215 30.04.2018 10:38:54 UTC Tites Peter (QRTPE0) Auto greaser replaced. Job completed
90487608 | 2018-04-30 | A081-1S0241 | 1S-0241 fiilter element to be replaced | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10264640 | 700002354895 | JFC CORPORATION | Integrity | 1557.1 | 22 | 66 | Product Contamination | Product Contamination- | Filter medium | Replace | 24.04.2018 16:34:18 UTC Prashant Tamhane (QRPTA0) Clear description of the problem. 1S-0241 filter DP is at higher side , filter element to cleaned/replaced. PEFS: T-13.370.089 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. DP high. What actions did you already take to solve the problem, share information. sap raised , reduced lean amine flow. Additional mitigations : X WPS/ Work instruction needed Product information : Product left in equipment lean amine Expected amount : Requester Name : Prashant Phone : 44032111
90487745 | 2018-12-06 | A081-FIRE HYDRANT | SCE FH18 monitor passing when activated | MX04 |  | Routine Wrk LvL 5 | 0 |  | FIRE HYDRANT | CM | UTL | 10264625 |  |  |  | 0 | 6 | 5 | Other - please specify in text field | Other - please specify in text field-valve passing | Other - please specify in text field | Other - please specify in text field | 24.04.2018 12:19:14 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in April 2018 for GTL Train 2 area, it was found that the monitor FH18 was passing at the joint when activated. FH18 is located in Road F-2 opposite 2K-3041. Find attached PEFS, location and specification details. PEFS: T4003202RevC_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90487746 | 2019-01-17 | A081-FIRE HYDRANT | SCE FH25 monitor passing when activated | MX04 |  | Routine Wrk LvL 5 | 0 |  | FIRE HYDRANT | CM | UTL | 10264627 |  |  |  | 68.12 | 3 | 5 | Fouling | Fouling-valve leaking | Valve internals | Field repair | 24.04.2018 12:24:25 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in April 2018 for GTL Train 2 area, it was found that the monitor of fire hydrant FH25 was passing at the joint when activated. FH25 is located in Road F-4 Tank 2T-1201. Find attached PEFS, location and specification details. PEFS: T4003201RevC_F001and T4364121RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90487747 | 2018-05-27 | A081-FIRE HYDRANT | SCE FH26 delivery valve 3 passing | MX04 |  | Routine Wrk LvL 5 | 0 |  | FIRE HYDRANT | CM | UTL | 10264628 |  |  |  | 0 | 0 | 0 |  |  |  |  | 24.04.2018 12:31:57 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in April 2018 for GTL Train 2 area, it was found that the 3rd 2.5 inch delivery valve (from left to right) was passing at fire hydrant FH26. FH26 is located in Road F-1 under BD pipe rack. Find attached PEFS, location and specification details. PEFS: T4003202RevC_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 11.11.2018 04:26:38 UTC Srinivasa Dandu (QRSDA3) Duplicate with WO 90455899
90487748 | 2018-12-06 | A081-FIRE HYDRANT | SCE FH31 monitor passing when activated | MX04 |  | Routine Wrk LvL 5 | 0 |  | FIRE HYDRANT | CM | UTL | 10264629 |  |  |  | 0 | 6 | 5 |  |  |  |  | 24.04.2018 12:36:23 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in April 2018 for GTL Train 2 area, it was found that the monitor of fire hydrant FH31 was passing at the joint when activated. FH31 is located in Road F-4 opposite 2C-3401. Find attached PEFS, location and specification details. PEFS: T4003201RevC_F001 and T4364121RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90487749 | 2018-12-06 | A081-FIRE HYDRANT | SCE FH46 monitor passing when activated | MX04 |  | UserDefined Priority | 0 |  | FIRE HYDRANT | CM | UTL | 10264723 |  |  |  | 0 | 6 | 5 |  | - | Other - please specify in text field | Other - please specify in text field | 25.04.2018 09:03:49 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in April 2018 for GTL Train 2 area, it was found that the monitor of fire hydrant FH46 was passing at the joint when activated. FH46 is located opposite Reactor 2R-1116. Find attached PEFS, location and specification details. PEFS: T4003201RevC_F001 and T4364121RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90487750 | 2018-09-24 | A081-FIRE HYDRANT | SCE FH47 winged cam faulty | MX04 |  | Routine Wrk LvL 5 | 0 |  | FIRE HYDRANT | CM | UTL | 10264724 |  |  |  | 144.84 | 4 | 4 | Normal Wear | Normal Wear-Due to wear | Fire water hydrant | Replace | 25.04.2018 09:07:54 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in April 2018 for GTL Train 2 area, it was found that the Winged Cam Assembly Kit at the 4th delivery valve (from left to right) of fire hydrant FH47 was faulty and needs to be replaced. The MM number for the spare part is10687723. FH47 is located in Road F6 opposite Finger 3. Find attached PEFS, location and specification details. PEFS: T4003201RevC_F001 and T4364121RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90487976 | 2018-05-13 | A081-1F5111 | 1F5111 Penthouse Grating to be fix.** | MX04 | M_FUR_X | Routine Wrk Lvl 2 | 0 |  | SMR FURNACE | CM | LPU | 10263484 | 700002348459 | KTI | Integrity | 118.87 | 8 | 12 | Other - please specify in text field | Other - please specify in text field-grating fall down | Other - please specify in text field | Fix / Repair | 12.04.2018 01:21:38 UTC Sandeep Shah (QRSSH8) Reformer Penthouse area one grating fallen down near burner no. K10. Grating to be reinstate and lock to be provided.
90488926 | 2018-05-07 | A081-0P2021 | ACC CLEANING PUMP ELECTRICAL TRIP | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10265519 | 700002199414 | PRATISSOLI | Rotating | 75.41 | 8 | 0 | Other - please specify in text field | Other - please specify in text field-Motor Tripped on Over Load | Other - please specify in text field | Fix / Repair | 06.05.2018 07:49:13 UTC Govindaraj Swaminathan (QRGSW0) Clear description of the problem. ACC CLEANING PUMP ON ASU $ TRIP DURING START AND NEEDS TO RESEET TO CONTINUE ACC CLEANING PEFS: Prioriteit: Additional mitigations : Requester Name : Swami Phone : 44032213 10.05.2018 12:52:51 UTC Mutharasu Subbaih (QRMSU8) Checked for Motor Tripping and found that motor was tipped on Thermal overlaod and the same was resetted and started found normal.
90489779 | 2018-05-30 | A081-0S8361A | MSDU CANNOT RUN DUE TO TRANSMITTER ISSUE | MX04 | E_MOT_LV | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10265804 | 700001730109 | ABB | Electrical | 415.53 | 12 | 12 | Mechanical damage | Mechanical damage-KM1 faulty. | Switchgear | Replace | 09.05.2018 01:39:31 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. Hi Aswin, Kindly provide support for tomorrow’s job. Operations can not start MSDU due to alarms indicated in the HMI(codes 67, 101 etc-can’t be reseted) and suspected one of the cause is the transmitter under the centrifuge motor that maybe faulty. So far we found normal in electrical side. Hi Ravi/SK, Please raise SAP notification. Thanks. Best regards, John D. Babate UTL/ASU Electrical Maintenance Office: +974 4403 2794/5 Personal Mob. # +974 5012 2891 Qatar Shell GTL P.O. Box 3747, Doha., Qatar PEFS: Prioriteit: Additional mitigations : Requester Name : Bagus Phone : 44032215
90490030 | 2018-09-08 | A081-0S0123A | 0S-0123A HC filter element repalcement | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10266238 | 700002201322 | DKME | Integrity | 7415.93 | 29 | 45 |  |  |  |  | 15.05.2018 06:13:42 UTC Sivakumar Manokaran (QRSMAA) 0S-0123A HC filter DP high need to replace the filter element.
90490031 | 2018-07-15 | A081-0S0163A | 0s-0163A HC filter element repalcement | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10266237 | 700002200042 | DKME | Integrity | 7527.34 | 29 | 45 | Product Contamination | Product Contamination- | Filter medium | Replace | 15.05.2018 06:08:18 UTC Sivakumar Manokaran (QRSMAA) U-0100 string-3 hydro carbon filter DP high need to replace the filter element.
90491473 | 2018-06-26 | A081-1SB210N2 | 1SB210N2-Q15_HPS 1, LIGHTING MCB TRIPPED | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10267178 | 700002352082 | ABB MALAYSIA | Electrical | 101.89 | 10 | 12 | Internal failure / short | Internal failure / short-Faulty circuit of lighting | Fuse / MCB | Check/ Inspect/ Test | 29.05.2018 10:06:41 UTC Michael I Dela Cruz (QRMDE6) Phone 44032804 Clear description of the problem. MCB TRIPPED FOR LIGHTING OF CIRCUIT 1SB210N2-Q15, AFFECTED AREA HPS 1, PH 1, 1R3024/3025/3026 AREA FROM GROUND TO TOP ELEVATION. NEED TO DO TROUBLE SHOOTING CAUSING THE TRIP AND RESET PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : MICHAEL Phone : 31548632 28.06.2018 04:51:44 UTC Mageshkumar Rajaram (QRMRA1) Phone 44032804 2804 Raised new notification:10269349 for 1LFN210N2-15-L2-08 250WATTS FLOOD LIGHT CAUSING THE TRIPPING OF THE CIRCUIT. DISCONNECTED FROM THE CIRCUIT(1JB7671047), LTG FIXTURE NOT WORKING NEED TO DO TROUBLE-SHOOTING/REPLACEMENT OF PARTS.
90491480 | 2018-06-05 | A081-0S0163B | 0S-163 BFilter replacement | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10267230 | 700002200043 | DKME | Integrity | 229.88 | 29 | 53 | Product Contamination | Product Contamination- | Filter medium | Replace | 30.05.2018 02:32:46 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163 B HC filter need to be replaced if it exhausts
90491485 | 2018-06-08 | A081-FIRE HYDRANT | SCE FH236 delivry end-cap seized-1B2 CHW | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10267163 |  |  |  | 0 | 6 | 12 | Poor installation | Poor installation- | cap | Adjust / align | 29.05.2018 05:17:45 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in May 2018 for FGP Train 2 area, it was found that the 5-inch delivery end-cap of fire hydrant FH236 was seized. FH 236 is located in Road F-18 opposite OE-7234 Find attached location map and photo. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90491486 | 2018-06-08 | A081-FIRE HYDRANT | SCE FH233 delivery end cap seized-1B2 | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10267162 |  |  |  | 0 | 6 | 12 | Poor installation | Poor installation- | cap | Adjust / align | 29.05.2018 05:13:46 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in May 2018 for FGP Train 2 area, it was found that the 5-inch delivery end-cap of fire hydrant FH233 was seized. FH233 located Road F-18 East end of KC structure. Find attached location map and photo. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90491492 | 2018-06-11 | A081-0S8361A | MSDU LIGHTING NOT WORKING F3 | MX04 | E_MOT_LV | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10267182 | 700001730109 | ABB | Electrical | 0 | 40 | 40 | Internal failure / short | Internal failure / short-Fixture 33 is faulty. | Other - please specify in text field | Replace | 29.05.2018 10:51:59 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. MSDU Lighthing in centrifuge room area not working, all lighthing will trip if we switch on switch for centrifuge room lighthing. PEFS: Prioriteit: Additional mitigations : Electrical tasks: Requester Name : Bagus Phone : 44032215
90491510 | 2018-05-31 | A081-1A8324 | RETA DAF SMALL WHEEL ABNORMAL SOUND | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10267019 | 700002348718 |  | Integrity | 739.1 | 37 | 21 | Normal Wear | Normal Wear-Roller damaged | Rotating element | Replace | 26.05.2018 20:32:02 UTC Raju Sutham (QRRSU3) Clear description of the problem. TRAIN-1 DAF SCRAPPER SMALL WHEEL MINOR ABNORMAL SOUND OBSERVED, TO BE CHECK BY RE PEFS: T-4.118.864 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. IF THE WHEEL DAMAGED SCRAPPER CANNOT POSSIBLE TO RUN, PROCESS UPSET IN BIOTREATER Additional mitigations : X Scaffold Electrical tasks: X E-isolation Product information : Product left in equipment SOOTY WATER Expected amount : Requester Name : Raju.s Phone : 44032215 30.05.2018 06:04:09 UTC Frank Faroj (QRFFA0)
90491794 | 2019-01-21 | A081-FIRE HYDRANT | SCE FH40 delivery valves seized/passing | MX04 |  | UserDefined Priority | 0 |  | FIRE HYDRANT | CM | UTL | 10264721 |  |  |  | 2433.7 | 8 | 13 |  |  |  |  | 25.04.2018 08:59:22 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in April 2018 for GTL Train 2was found that valve 1 and 4 (from left to right) of fire hydrant FH40 was seized and passing. SAP WO 10249943 and 1024994 was raised on the 15/11/17 for the passing. FH40 is located in Road F-6 opposite Reactor 2R-1111. Find attached PEFS, location and specification details. PEFS: T4003201RevC_F001 and T4364121RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 11.11.2018 04:22:23 UTC Srinivasa Dandu (QRSDA3) Duplicate with WO 90460818
90491913 | 2018-07-21 | A081-0S8361A | PMFL-0SM-8361A1-COOLING FAN FINS DAMAGED | MX04 | E_MOT_LV | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10267399 | 700001730109 | ABB | Electrical | 219.49 | 20 | 22 | end of life | end of life- | Fan | Replace | 31.05.2018 16:05:27 UTC V. Velyogeeswaran (QRVVE2) Phone 4403 2795 Clear description of the problem. DURING PM FOUND MOTOR COOLING FAN FINS GOT DAMAGED CONDITION,NEED TO BE REPLACED MATERIAL NO:-10629055 REF MX01 NO-90477750 PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : VENAKTESAN 22.07.2018 02:30:01 UTC V. Velyogeeswaran (QRVVE2) Phone 4403 2795 fan replaced with new
90491993 | 2018-07-21 | A081-1A8324 | RETA;FIX THE DAMAGE GREASE TUBE,1A-8324 | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10267651 | 700002348718 |  | Integrity | 505.48 | 102.5 | 102.5 | Other - please specify in text field | Other - please specify in text field-long time useing | Other - please specify in text field | Replace | 03.06.2018 04:35:05 UTC Baskar Selvam (QRBSE0) 03.06.2018 04:21:40 UTC Baskar Selvam (QRBSE0) Clear description of the problem. To be fixed back the removed grease tube for 1A-8324 FFU center bearing Grease tube found detached from the bearing housing , Lubrication is not happening for the central bearing, which can damage if the lubrication is not going in. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : BASKAR-RE Phone : 66946260 20.10.2018 11:20:44 UTC SREENIVASA LAKKARAJU (QRSLA4) fixed back the removed grease tube for 1A-8324 FFU center bearing Grease tube found detached from the bearing housing , job completed
90492239 | 2019-02-03 | A081-294XA-50200-S | 2ET-LPU-001 EHT FAULT TR2; CHK | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10267173 | 700002607282 |  | Instrumentation | 337.27 | 66 | 150 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault- | Heat Tracing | Field repair | 29.05.2018 09:16:06 UTC Jayantilal Patel (QRJPA5) Clear description of the problem. 294XA50200 EHT common fault alarm, frequent sound coming Prioriteit: Additional mitigations : Requester Name : Lester Phone :44032413
90492819 | 2018-10-20 | A081-0S0123B | 0S-123B DP high-> | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10268210 | 700002200643 | DKME | Integrity | 17948.24 | 29 | 53 |  |  |  |  | 10.06.2018 11:28:29 UTC Elangovan Muthusamy (QREMU0) 0S-123B DP high filter element to be replaced.
90492838 | 2018-07-01 | A081-2A8324 | 2A-8324 GEAR BOX TO BE REPLACED HSOS | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10268196 | 700002297332 |  | Integrity | 644.26 | 114 | 84 |  |  |  |  | 10.06.2018 09:24:51 UTC Srinivasan Ramasamy (QRSRAE) Clear description of the problem. 2A-8324 DAF SCRAPPER GEARBOX TO BE REPLACED WITH ORIGINAL GEAR BOX AS PER DESIGN. PEFS: T-4.118.867 Prioriteit: Additional mitigations : X JHA needed Requester Name : Srinivasan Ramasamy Phone : 66675065 06.07.2018 00:02:15 UTC Tites Peter (QRTPE0) Replaced with new gear box . Job completed
90494077 | 2018-06-24 | A081-0X0104 | 0S-104 Screw conveyor cleaning | MX09 | E_MOT_LV | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10268910 | 700002203439 | DRM LOHER | Electrical | 0 | 10 | 14 | Other - please specify in text field | Other - please specify in text field-celluloose dumped on conveyor | Other - please specify in text field | Check/ Inspect/ Test | 20.06.2018 12:08:02 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0X-104 Screw conveyor of Dr.M filter need to be cleaned before next precoat preparation. Location--Dr.M filter near 0V-0103.
90494612 | 2018-07-18 | A081-0X0104 | 0X-104 screw conveyor view glass crack | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10269324 | 700002206193 |  | Electrical | 402.43 | 6 | 12 | improper set up | improper set up-Improper celullose batch sequence logic | conveyors | Replace | 26.06.2018 22:22:10 UTC Elangovan Muthusamy (QREMU0) 0X-104 screw conveyor view glass got crack while first bag loading and FO stopped from field. the same conveyor two days back cleaned for batch preparation. to be replaced and precoat preparation is hold.
90494764 | 2018-08-23 | A081-0X0104 | 0X-104 screw conveyor cleaning | MX09 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10269421 | 700002206193 |  | Electrical | 0 | 6 | 15 | Other - please specify in text field | Other - please specify in text field-Logic during loading cellulose | Other - please specify in text field | Cleaned | 27.06.2018 23:56:38 UTC Elangovan Muthusamy (QREMU0) 0X-104 screw conveyor to be cleaned for next batch preparation
90494772 | 2018-08-20 | A081-FIRE HYDRANT | SCEI-FH361 DELIVRY VLV ENDCAP SEIZED;TF* | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10269397 |  |  |  | 50.81 | 6 | 13 | Normal Wear | Normal Wear- | Other - please specify in text field | Field repair | 27.06.2018 09:59:36 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in June 2018 for LPU Tankfarm, it was found that the first (from left to right) 2.5inch delivery end cap of FH361 was seized. FH361 is located in Road A Find attached PEFS, location and specification details. PEFS: T4364120RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90494777 | 2018-08-20 | A081-FIRE HYDRANT | SCEI-FH423-5" DELIVERY ENDCAP SIEZED;TF* | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10269396 |  |  |  | 40.65 | 12 | 13 | Normal Wear | Normal Wear- | Other - please specify in text field | Field repair | 27.06.2018 09:48:00 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in June 2018 for LPU Tankfarm, it was found that the LDH 5inch end cap of FH423 was seized. FH423 is located in Road B opposite FAR15. Find attached PEFS, location and specification details. PEFS: T4364120RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90494778 | 2018-07-18 | A081-FIRE HYDRANT | SCEI-FH168 MONITOR NOZZLE SIEZED;2F5111 | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10269394 |  |  |  | 0 | 9 | 13 | Other - please specify in text field | Other - please specify in text field-FH monitor swivel joint seized | Fire water monitor | Fix / Repair | 27.06.2018 08:43:47 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in June 2018 for LPU Train 2 area, it was found that the monitor nozzle of FH168 was seized. FH168 is located in 4th Ave, opposite 2F-5111. Find attached PEFS, location and specification details. PEFS: T4100323RevC_F001 <(>&<)> T4364121RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90494781 | 2018-07-17 | A081-FIRE HYDRANT | SCEI-FH160 END CAP 1DELVRY SEIZED;TR2** | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10269384 |  |  |  | 0 | 9 | 13 | Other - please specify in text field | Other - please specify in text field-seized due to dirt & dust | Fire water hydrant | Fix / Repair | 27.06.2018 08:21:32 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in June 2018 for LPU Train 2, it was found that the end cap of the first delivery (from left to right) was seized of fire hydrant FH160 (see attached photo). FH160 is located in LPU Train 2, EC area, junction of 6th Ave and Road F-12. Find attached photo, location and specification details. PEFS: T4364121RevO_F001 <(>&<)> T4100323RevC_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90494783 | 2018-07-17 | A081-FIRE HYDRANT | SCEI-FH163 MONITOR SEIZED;SMR2 AH36** | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10269382 |  |  |  | 0 | 9 | 13 | Lack of lubrication | Lack of lubrication- | mechanical part | Fix / Repair | 27.06.2018 08:13:21 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in June 2018 for LPU Train 2, it was found that the monitor nozzle was seized of fire hydrant FH163 (see attached photo). FH163 is located in LPU Train 2, EC area, near Analyzer House #36. Find attached photo, location and specification details. PEFS: T4364121RevO_F001 <(>&<)> T4100323RevC_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90494785 | 2018-07-17 | A081-FIRE HYDRANT | SCEI-FH062 MONITOR SEIZED 2V4401 AREA** | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10269379 |  |  |  | 0 | 9 | 13 | Lack of lubrication | Lack of lubrication- | mechanical part | Fix / Repair | 27.06.2018 08:03:37 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in June 2018 for LPU Train 2, it was found that the monitor nozzle was seized of fire hydrant FH062 (see attached photo). FH062 is located in LPU Train 2, EA area, opposite 2V-4401. Find attached photo, location and specification details. PEFS: T4364121RevO_F001 <(>&<)> T4364121RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90494950 | 2018-11-22 | A081-2SB200N2 | Repair/ Re-route the Cable Tray | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10269432 | 700002373557 | ABB MALAYSIA | Electrical | 18.45 | 2 | 4 | Mechanical damage | Mechanical damage- | Cable / Terminations | Check/ Inspect/ Test | 28.06.2018 06:41:06 UTC Hari Subono (QRHSU0) Clear description of the problem. Cable Tray cover just beside the lifting zone is bend and open. PEFS: Prioriteit: X Scaffold X Insulation Requester Name : Hari Subono Phone : 33392562 02.07.2018 12:01:22 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 EQUIPMENT CODE- A081-2SB200N2 - LIGHTING RELATED
90494989 | 2018-11-22 | A081-2SB200N2 | Repair/ Re-route Cable Tray | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10269433 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 2 | 8 | Mechanical damage | Mechanical damage-Slightly bended | Cable / Terminations | Check/ Inspect/ Test | 28.06.2018 06:50:43 UTC Hari Subono (QRHSU0) Clear description of the problem. The Cable tray beside the lifting zone is bend & open. PEFS: Prioriteit: X Scaffold X Insulation Requester Name : Hari Subono Phone : 33392562 02.07.2018 11:59:38 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 EQUIPMENT CODE- A081-2SB200N2 - LIGHTING RELATED
90495662 | 2018-07-18 | A081-0S0163A | 0S-163 A Filter replacement | MX04 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10269972 | 700002200042 | DKME | Integrity | 0 | 0 | 0 |  |  |  |  | 04.07.2018 10:22:42 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163 A Hydrocarbon filter in U-100 String-3 filter need to be replaced after exhaustion.
90495808 | 2018-07-10 | A081-0X0104 | 0X-104 screw conveyor cleaning | MX04 | E_MOT_LV | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10269974 | 700002203439 | DRM LOHER | Electrical | 0 | 6 | 12 | Overload | Overload- | Other - please specify in text field | clean | 04.07.2018 11:05:34 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0X-104 screw conveyor of Dr.M filter need to be cleaned before batch preparation to avoid damage to glass cover
90497208 | 2018-07-22 | A081-2A8324 | 2AM-8324 VSD MOTOR COMMON ALARM STANDING | MX04 | E_MOT_LV | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10270514 | 700002297890 | ABB | Electrical | 31.52 | 6 | 18 | Lack of lubrication | Lack of lubrication-Gear box oil level low. | Protection Relay / MCU | Repair / correct | 11.07.2018 09:23:44 UTC Srinivasan Ramasamy (QRSRAE) Clear description of the problem. 2AM-8324 DAF SCRAPPER VSD MOTOR OFFNRM HIGH PRIORITY COMMON ALARM STANDING, ELECTRICAL NEED TO CHECKED IN VSD PANEL. 2A-8324 IN SERVICE AND RUNNING NORMAL. PEFS: T4.118.867 Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. 2A-8324 DAF SCRAPPER SPEED REDUCED TO AVIOD MOTOR DAMAGE. Electrical tasks: X E-isolation Requester Name : Srinivasan Ramasamy Phone : 66675065 06.09.2018 11:46:44 UTC Rakeshkumar Patel (QRRPA1) Checked found gear box oil level low topup done by RE, trial taken ok. Attened with SB WO-90505421
90497482 | 2018-08-03 | A081-0S0163B | 0S-163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10270589 | 700002200043 | DKME | Integrity | 254.93 | 29 | 53 |  |  |  |  | 12.07.2018 09:13:28 UTC Elangovan Muthusamy (QREMU0) 0S-163B DP high filter element to be replaced.
90498669 | 2018-08-08 | A081-1F5111 | TR1 1F5111 PORTABLE IGNITOR NOT WKG | MX04 | M_FUR_X | Routine Wrk Lvl 2 | 0 |  | SMR FURNACE | CM | LPU | 10271410 | 700002348459 | KTI | Integrity | 0 | 24 | 22 | Power failure | Power failure-Control Card Failure | Burner - cup throat | Test | 22.07.2018 00:30:03 UTC Ramesh Thangavelu (QRRTH1) Train1 SMR Furnace Portable Ignitor Not working. Ignitor Kept in CCR PTL room. 09.12.2018 08:20:46 UTC Premkumar Dayalan (QRPDA2) Phone 70480663 Replaced Battery and checked, but not working due to Electronic board faulty.
90498670 | 2018-07-21 | A081-0S8361A | MSDU WATER PUMP M302 TRIPPING | MX04 | E_MOT_LV | Emergency | 0 |  | CENTRIFUGE | CM | ETP | 10271409 | 700001730109 | ABB | Electrical | 530.36 | 187 | 12 | end of life | end of life-IGBT blower fan failed | Fan | Check/ Inspect/ Test | 21.07.2018 22:58:41 UTC Raju Sutham (QRRSU3) Clear description of the problem. MSDU WATER PUMP M302 NOT GETTING START,NEED TO ATTEND PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. MSDU NOT POSSIBLE TO START, TANK LEVEL HIGHER SIDE Additional mitigations : Requester Name : Raju.s Phone : 44032215 23.07.2018 22:31:58 UTC John Babate (QRJBA6) Notif created (10271560) for overhauling, testing, installation, cable reconnection and final testing. 29.07.2018 04:24:50 UTC Joly Poulose (QRJVI4) VSD Blower fan replaced with new one due to over heating of VSD.
90498864 | 2018-08-08 | A081-1F5111 | PIGTAIL INSPECTION FOR SMR TRAIN-1 | MX09 | M_FUR_X | Routine Wrk Lvl 1 | 0 |  | SMR FURNACE | CM | LPU | 10271482 | 700002348459 | KTI | Integrity | 9021.6 | 0 | 0 |  |  |  |  | 22.07.2018 12:42:08 UTC Arun Kadam (QRAKA6) Clear description of the problem. IF-5111 PIG TAIL INSPECTION PEFS: T-4.343.604 Prioriteit: Additional mitigations : Requester Name : Arun Kadam Phone : 44032411 23.07.2018 10:14:29 UTC Muthu Siva Krishnan Kalyani Rao (QRMKA2) The pigtails are to be
90499017 | 2018-09-15 | A081-2SB200N2 | NEAR 2R-3121 CABLE TRAY COVER DAMAGE | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10271538 | 700002373557 | ABB MALAYSIA | Electrical | 137.02 | 12 | 46 | Human Error | Human Error- | Casing / enclosure | Replace | 23.07.2018 11:54:29 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER WO- 90491079 VISUAL INSPECTION DONE, FOUND 50MM CABLE TRAY COVER FOUND DEFORMED FROM ITS POSITION DUE TO SOME OBJECT HITTING ON IT, NEED TO REMOVE AND REPAIR/ REPLACEMENT REQUIRED. SCAFFOLDING REQUIRED AT 10 MTS NEAR TO 2R-3121 WEST SIDE STAIR CASE FOR RECTIFICATION. PEFS: - Prioriteit: X Scaffold Electrical tasks: X JHA needed Requester Name : PRABAKARAN Phone : 44032804 24.07.2018 06:33:17 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 EQUIPMENT CODE CHANGED TO A081-2SB200N2
90499353 | 2018-08-06 | A081-0S8361A | O/H OF MOTOR AT MANWEIR- CM#90498670 | MX20 | E_MOT_LV | Routine Wrk LvL 5 | 0 |  | CENTRIFUGE | CM | ETP |  | 700001730109 | ABB | Electrical | 617 | 0 | 1
90500470 | 2018-08-06 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10272075 | 700002200042 | DKME | Integrity | 313.83 | 27 | 46 |  |  |  |  | 31.07.2018 07:06:03 UTC Amit Gaur (QRAGA0) 0S-0163B filter element replacement
90500472 | 2018-08-17 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10272076 | 700002202402 | DKME | Integrity | 582.69 | 27 | 45 |  |  |  |  | 31.07.2018 07:08:14 UTC Amit Gaur (QRAGA0) 0S-0143A filter elemtn replacment
90500695 | 2018-08-12 | A081-0S8361A | MSDU AUTO GREASING LEVEL LOW | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10272168 | 700001729713 |  | Rotating | 70.53 | 0 | 8 | Lack of lubrication | Lack of lubrication-Low greaser in auto greaser | Bearing | Replace | 01.08.2018 05:33:58 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. MSDU auto greasing level low, need to be replaced with new grease tube. PEFS: MSDU Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : Bagus Phone : 44032215 11.08.2018 23:35:33 UTC Rajeshwar Prasad (QRRPR1) Phone 33003359 Removed the old greaer and fixed the new auto greaser with new battery. old battery was showing red, after replacement, now it is showing green. fixed the auto greaser on the bearing. job completed.
90502419 | 2018-08-21 | A081-1F5111 | 1F5111 THERMOGRAPHY -MAINT. SUPPORT | MX04 | M_FUR_X | Routine Wrk Lvl 1 | 0 |  | SMR FURNACE | CM | LPU | 10272430 | 700002348459 | KTI | Integrity | 2166.83 | 160 | 240 | Preventive Maintenance Work | Preventive Maintenance Work-IR scanning only | Furnace tube | Inspect | 05.08.2018 06:52:58 UTC Nagamalleswara Rao (QRNRA0) Clear description of the problem. 1F-5111 THERMOGRAPHY PLANNED. MAINTENENCE SUPPORT REQUIRED TO OPEN PEEPHOLE WINDOW GLASSES. PEFS: T-13.370.743 Prioriteit: X JHA needed Requester Name : MALLESH Phone : 44032411
90502421 | 2018-08-13 | A081-294XA-50200-S | 2ET-LPU-001 EHT ALARM-DU | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10272230 | 700002607282 |  | Instrumentation | 0 | 0 | 0 |  |  |  |  | 01.08.2018 21:34:13 UTC Gopinath Kokoori Vadakkethil (QRGVA2) 2ET-LPU-001 electric trcng cammon fail alarm; Both main and Red taken in line, both on alarm, pl attend
90502782 | 2018-12-15 | A081-FIRE HYDRANT | SCE FH440 5 INCH DELIVERY DAMAGED-ETU | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10272419 |  |  |  | 2802.27 | 6 | 13 | Normal Wear | Normal Wear- | Other - please specify in text field | Replaced | 05.08.2018 05:09:03 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in July 2018 for FGP Train 1, it was found that the bottom high volume 5 inch delivery at hydrant FH440 was damaged (see attached photo). FH440 is located in Road C opposite main structure. The spare part MM number is 10574063. Find attached PEFS, location, photos and specification details. PEFS: T4364121RevO_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90505290 | 2018-09-09 | A081-1F5111 | 1F5111 BURNER CLEANING 2018 | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU |  | 700002348459 | KTI | Integrity | 0 | 0 | 0
90505304 | 2018-08-15 | A081-0S0143A | 0S-0143A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10272746 | 700002201324 | DKME | Integrity | 4411.19 | 27 | 46 |  |  |  |  | 09.08.2018 07:45:07 UTC Sivakumar Manokaran (QRSMAA) U-0100, STR-2, HYDRO CARBON FILTER 0S-0143A DP IS HIGH NEED TO REPLACE THE FILTER ELEMENT REPLACEMENT.
90505305 | 2018-08-15 | A081-0S0163B | 0S-0163B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10272745 | 700002200043 | DKME | Integrity | 254.93 | 22 | 40 |  |  |  |  | 09.08.2018 07:42:48 UTC Sivakumar Manokaran (QRSMAA) U-0100, STR-3, HYFRO CARBON FILTER 0S-0163B DP IS HIGH NEED TO REPALCE THE FILTER ELEMENT.
90505421 | 2018-08-12 | A081-2A8324 | DAF2 SCRAPPER TRIP -MOTOR VSD ALARM FO1 | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10272807 | 700002297890 | ABB | Electrical | 382.97 | 28 | 24 | Overload | Overload- | Invertor | Adjust / reset | 10.08.2018 01:40:41 UTC Eric Ates (QREAT0) Clear description of the problem. DAF2 SCAPPPER MOTOR OBSERVED VSD COMMON ALARM, 2A8324 VSDRO COMMON ALARM.EARLIER COMMON ALARM ALSO CHECKED BY ELECTRICAL AND RECTIFI ED.AGAIN IT IS COMING. PEFS: T-4.118.867 Prioriteit: Additional mitigations : Electrical tasks: Requester Name : ERIC ATES Phone : 44032215 11.08.2018 00:19:02 UTC "Lourdhu Ponnusamy, " Thomas (QRTPO0) NOW THE DAF-2 SCRAPPER IS NOT RUNNING DUE TO THIS ALARM AND TO BE FIXED IMMEDIATELY. 11.08.2018 12:35:49 UTC V. Velyogeeswaran (QRVVE2) Phone 4403 2795 Checked <(>&<)> found vsds tripped on +MOTOR TEMP(4310),checked the motor IR/WR values(IR-816MΩ,WR-34.2Ω balance) ,found ok <(>&<)> compare the fault function parameters 30.04 to 30.09 with 1VS200N8324A,found ok Reset <(>&<)> trial taken, Now running normal with RLA-1.85A ,torque-40%(FLA-1.9A,kw-1.5) Under observation..Eptw-214796-suspended 13.08.2018 13:25:43 UTC V. Velyogeeswaran (QRVVE2) Phone 4403 2795 trip reset <(>&<)> trial taken today again,but bridge is not moving,so
90505452 | 2018-08-25 | A081-0X0104 | 0X-104 screw conveyor cleaning | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10272916 | 700002206193 |  | Electrical | 61.8 | 6 | 12 | Fouling | Fouling-start up | Other - please specify in text field | Cleaned | 11.08.2018 11:37:57 UTC Elangovan Muthusamy (QREMU0) 0X-104 screw conveyor to be cleaned for Dr M filter batch preparation
90505466 | 2018-08-18 | A081-0S0163A | 0S-0163A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10272818 | 700002200042 | DKME | Integrity | 7072.17 | 22 | 41 |  |  |  |  | 10.08.2018 05:45:44 UTC Sivakumar Manokaran (QRSMAA) 0S-0143B filter DP is high need to replace the filter element 12.08.2018 04:56:27 UTC Prakashchandra Patel D (QRPPA4) 0S-0163A filter element change
90507802 | 2018-12-11 | A081-0S0163A | 0S-163A DP HIGH-> | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10273210 | 700002200042 | DKME | Integrity | 225.09 | 23 | 40 |  |  |  |  | 15.08.2018 20:21:28 UTC Elangovan Muthusamy (QREMU0) 0S-163A DP high filter element to be replaced.
90507804 | 2018-12-10 | A081-0S0163B | 0S-163B DP HIGH-> | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10273211 | 700002200043 | DKME | Integrity | 0 | 24 | 42 |  |  |  |  | 15.08.2018 20:23:37 UTC Elangovan Muthusamy (QREMU0) 0S-163B DP high filter element to be replaced.
90507809 | 2018-09-12 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10273208 | 700002201324 | DKME | Integrity | 0 | 22 | 41 |  |  |  |  | 15.08.2018 20:19:38 UTC Elangovan Muthusamy (QREMU0) 0S-143A DP high filter element to be replaced.
90507811 | 2018-08-24 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10273209 | 700002202402 | DKME | Integrity | 13445.21 | 21 | 39 |  |  |  |  | 15.08.2018 20:20:18 UTC Elangovan Muthusamy (QREMU0) 0S-143B DP high filter element to be replaced.
90507984 | 2019-04-10 | A081-1F5111 | POOR LIGHTING 1F5111 AIR DUCT AREA* | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10272872 | 700002348459 | KTI | Integrity | 101.88 | 56 | 128 | end of life | end of life- | Lamps | Replace | 10.08.2018 23:09:42 UTC Darwin Montanez (QRDMO1) Clear description of the problem. 1E5111 Combustion air, flue gas and heat recovery ducts area from ground floor up to the platforms. A total of ten 10.0 fixtures tube lighting to be replaced. PEFS: T-4.107.000 Prioriteit: Requester Name : Ferdinand Balinos Phone : 6648 0081
90508065 | 2018-08-20 | A081-0S8361A | MSDU FLOC DOSING LINE DRAIN NIPPLE BROKE | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10273371 | 700001729713 |  | Rotating | 1073.34 | 0 | 0 |  |  |  |  | 18.08.2018 13:35:34 UTC Joyabrata Gupta (QRJGU0) Clear description of the problem. MSDU FLOCCULANT DOSING PVC LINE DRAIN NIPPLE GOT BROKEN. Prioriteit: Additional mitigations : X WPS/ Work instruction needed X LOTO/Spading X Block and bleed Electrical tasks: X E-isolation Requester Name : gupta Phone : 44032215 19.08.2018 12:16:31 UTC Frank Faroj (QRFFA0) MSDU OUT OF SERVICE DUE TO THIS LEAK, SLUDGE TANK LEVEL HIGH AND PLANT LOAD 100% , CAN WAIT FOR 10 DAYS TO ATTEND THIS LEAK. 20.08.2018 23:43:09 UTC Tites Peter (QRTPE0) Floc dosing line repaired and fixed back. Job completed
90508068 | 2018-09-01 | A081-1A8324 | DAF TRAIN 1 SCRAPER SUPORT WELDING BROKE | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10273370 | 700002348718 |  | Integrity | 1005.58 | 61.5 | 58.5 | Other - please specify in text field | Other - please specify in text field- | Other - please specify in text field | Fix / Repair | 18.08.2018 13:24:16 UTC Joyabrata Gupta (QRJGU0) Clear description of the problem. TRAIN 1 FFU DAF SCRAPPER ONE L SUPPORT ARM WELDING JOINT GOT DETACHED. PEFS: T-4.118.864 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X Scaffold Electrical tasks: X E-isolation Requester Name : gupta Phone : 44032215 25.11.2018 12:35:16 UTC Vudumudi Ravikumar (QRRVU1) PH-1 scrapper scum board support removed, welding done, QC Inspection and fixed back
90508491 | 2019-02-02 | A081-2A8324 | DAF2 BLOWDOWN LINE MANUAL VALVE PASSING | MX04 | M_X_X | Routine Wrk LvL 5 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10273504 | 700002297332 |  | Integrity | 2727.46 | 499 | 503 | Normal Wear | Normal Wear- | Valves | Replace | 21.08.2018 08:47:08 UTC Srinivasan Ramasamy (QRSRAE) Clear description of the problem. DAF TR2 BOTTOM BLOWDOWN LINE KS VALVE 283KS20011 UPSTREAM MANUAL ISOLATION VALVE UNABLE TO CLOSE FULLY, STUCK AT 40% OPEN AND OBSERVED VALVE PASSING.THIS JOB CAN BE DONE ONLY DURING TA OR DAF OUTAGR. VALVE LOCATED INSIDE CONFINED SPACE AND SCAFFOLDING REQUIRED. PEFS: T-4.118.867 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X Scaffold Requester Name : SRINIVASA RAMASAMY Phone : 44032215 11.03.2019 07:25:32 UTC Paranthaman Palanisami (QRPPA1) DAF-2 Manual Drain valve Passing (DN100 cl 150) (Butterfly valve). During valve Replacement activity identified that valve was stuck up. With butterfly valve open condition unable to do replacement, so the GRVE pipe was cut as nearest after discussion with SME. ITP prepared and approved by Integrity. After valve replacement the same line GRVE Wrapping completed by PGCC Contractor. Job completed and Handover to Operation
90508492 | 2018-08-24 | A081-0S8361A | MSDU CENTRI NDE ABNORMAL SOUND | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10273626 | 700001729713 |  | Rotating | 3290.57 | 24 | 24 |  |  |  |  | 23.08.2018 12:12:43 UTC Eric Ates (QREAT0) Clear description of the problem. MSDU CENTRIFUGE NDE BEARING DAMAGED CONDITION.NEEDS TO BE REPLACE AS PER RE.RE ALREADY CHECKED AND CONFIRMED BEARING IS DAMAGED.NOTE: MSDU PEFS NOT AVAILABLE IN AIMS. PEFS: Prioriteit: Additional mitigations : X WPS/ Work instruction needed X Scaffold Requester Name : ERIC ATES Phone : 44032215 17.09.2018 08:28:54 UTC Frank Faroj (QRFFA0) LOAD OF SLUDGE 100% AND SUD NOT ABLE TO MANAGE THIS LOAD, SO RAISE SB WOR ORDER FOR MSDU.
90508737 | 2018-09-10 | A081-2SB200N2 | BA AREA LTG. 2SB200N2-CKT. 06_FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10273837 | 700002373557 | ABB MALAYSIA | Electrical | 202.89 | 16 | 24 | Loose connection | Loose connection- | Lamps | Repair / correct | 27.08.2018 03:03:29 UTC Michael I Dela Cruz (QRMDE6) Phone 44032804 Clear description of the problem. MCB TRIPPED FOR LIGHTING 2SB200N2-CKT 06. AFFECTED LOCATION BA AREA GROUND LEVEL( 2V8161, 2E811A/B, 2V8111, 2V8112, AH08). NEED TO DO TROUBLESHOOTING TO ISOLATE/DISCONNECT FAULTY CIRCUIT. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-Disconnect X E-isolation Requester Name : MICHAEL Phone : 31548632
90508969 | 2018-09-05 | A081-294XA-50200-S | 2ET-LPU-001 EHT FAULT ALM;BOTH;HSE | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10273959 | 700002607282 |  | Instrumentation | 4603.06 | 67 | 221 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault- | Heat Tracing | Hardware Replacement | 28.08.2018 14:02:06 UTC Nagamalleswara Rao (QRNRA0) Clear description of the problem. 294XA-50200 ELLECTRICAL HEAT TRACING COMMON ALRM FUALT FREQUENTLY APEARING, TAG NO-2ET-LPU-001 SWITCH NO-2SW-7302211 (2RX-4001 TOP P LATFORM) PEFS: Prioriteit: Additional mitigations : X Scaffold X Insulation Electrical tasks: X E-Disconnect X JHA needed Requester Name : MANIK KALITA Phone : 44032413 04.10.2018 12:09:22 UTC Sandipbhai Patel (QRSPB1) Both ECM Replaced and functional test completed confirm with Paanel operator and at control panel no alarm exist
90509317 | 2018-09-24 | A081-2SB200N2 | BD PIPERACK_BUSTED FLOURECENT LIGHT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10274284 | 700002373557 | ABB MALAYSIA | Electrical | 1607.19 | 30 | 38 | end of life | end of life- | Lamps | Replace | 31.08.2018 01:53:35 UTC Michael I Dela Cruz (QRMDE6) Phone 44032804 Clear description of the problem. BUSTED FLOURECENT TUBE LIGHT IN BD_PIPERACK GROUND FLOOR-NORTH SIDE. 16 UNIT X 18WATTS, 1 UNIT X 36WATTS. 3 METER ELEVATION, WITH GRAVEL ON THE FLOOR(NEED ADDITIONAL MITIGATION IF USIING LADDER) PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : MICHAEL Phone : 31548632 03.09.2018 07:42:37 UTC Nilesh Pathak (QRNPA2) MM-10650693 ETA 30.10.2018 HENCE WMAT 04.09.2018 12:27:28 UTC Nilesh Pathak (QRNPA2) MM-10650693 can be booked in lot of 30 only. Surplus material to be used for other WOs.
90510633 | 2018-09-23 | A081-FIRE HYDRANT | SCE FH479 is obstructed | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10274655 |  |  |  | 0 | 0 | 0 |  |  |  |  | 04.09.2018 07:42:53 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in August 2018 for GTL Train 1, it was found that the 5 inch LDH connection of FH479 is obstructed due to hydrant tilting as the ground base is sinking. (see attached photo). DR008 is located in Road C3 AD Pipe Rack opposite 1K - 3401. See attached map with marked location. It is recommended to remove the barrier which is blocking the hydrant as an interim measure until the civil construction can commence. PEFS: T4003102RevD_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 15.01.2019 06:54:08 UTC Sankaran Kutty Marar Muraleedharan (QRSMU4) From: Gaigher, Leo QSGTL-IGQ/SSF Sent: Monday, January 14, 2019 11:34 AM To: PEEDIKAYIL, SAEED QSGTL-IGQ/PM3 <(><<)>SAEED.PEEDIKAYIL@shell.com> Subject: CM notification 10274655 Good day Saeed,
90510634 | 2019-02-02 | A081-FIRE HYDRANT | SCE DR008 inlet damage GTL1 | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10274654 |  |  |  | 120.43 | 10 | 11 |  |  |  |  | 04.09.2018 07:38:35 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in August 2018 for GTL Train 1, it was found that the right-hand side inlet of dry-riser DR008 is physically damaged and can't be connected to the fire-hose (see attached photo). DR008 is located in Area AB, Plant Road C22, 1R - 3025. See attached map with marked location. PEFS: T4003102RevD_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 15.01.2019 04:43:29 UTC SAEED PEEDIKAYIL (QRSPE5) Line No:100-1W800563-18011Q1-N
90510696 | 2018-09-24 | A081-1F5111 | 1F5111 BURNER CLEAN;OCT2018~2019* | MX09 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10272615 | 700002348459 | KTI | Integrity | 64058.23 | 3160 | 4019 |  |  |  |  | 07.08.2018 10:26:09 UTC Darwin Montanez (QRDMO1) Clear description of the problem. 1F5111 burner cleaning is required as per Tech advice. HVAC needed. PEFS: T-13.370.604 Prioriteit: Requester Name : Darwin Montanez Phone : 44032411
90511440 | 2018-09-18 | A081-0P2021 | ASU - FABRICATE POWER WASHER FITTING | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10275686 | 700002199414 | PRATISSOLI | Rotating | 0 | 8 | 24 | Normal Wear | Normal Wear- | Other - please specify in text field | Fix / Repair | 17.09.2018 12:51:52 UTC Jonathan Yutiga (QRJYU0) Clear description of the problem. ASU6: ACC CLEANING KIT PUMP 0P2021 LEAK AT THE WATER SUPPLY FITTING. PEFS: Prioriteit: Additional mitigations : Requester Name : AZHAR Phone : 44032214
90511709 | 2018-12-23 | A081-0P2021 | ASU PH2 0P2021 OVERHAULING | MX04 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10275738 | 700002199414 | PRATISSOLI | Rotating | 3281.13 | 128 | 272 |  |  |  |  | 18.09.2018 09:45:05 UTC Bala Subramanian (QRBSU0) Clear description of the problem. ASU PH2 ACC CLEANING PUMP 0P2021 OVERHAULING TO BE DONE. PEFS: Prioriteit: Additional mitigations : Requester Name : BALASUBRAMANIAN Phone : 44032213
90512812 | 2018-01-01 | A081-0S0143B | 0S-0143B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10276627 | 700002202402 | DKME | Integrity | 198.57 | 27 | 46 |  |  |  |  | 30.09.2018 11:43:57 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) Clear description of the problem. 0S-143 B hydro carbon filter replacement . PEFS: T-4.094.330 Prioriteit: Requester Name : PRABU SANKAR Phone : 44032115
90514233 | 2018-11-12 | A081-0S0123B | 0S-0123B HC FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10277684 | 700002200643 | DKME | Integrity | 536.51 | 27 | 55 |  |  |  |  | 13.10.2018 13:11:52 UTC Sivakumar Manokaran (QRSMAA) U-0100, STR-1 Hydrocarbon filter 0S-0123B going to choke DP is increasing currently 1.9 barg. need to repalce the filter element
90515499 | 2018-11-03 | A081-294XA-50200-S | 294XA50200 COMN FAULT ALM IN PANEL | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10278569 | 700002607282 |  | Instrumentation | 0 | 6 | 6 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault- | Heat Tracing | Other - please specify in text field | 22.10.2018 12:54:26 UTC Santosh Naik (QRSNA3) Clear description of the problem. 294XA50200-- urgent priority alarm exist on 4B1 panel.Checked by FO in SS and observed some ENMC panel fault alarm.To be checked and attended.It is not tracing alarm. PEFS: Prioriteit: Additional mitigations : Requester Name : santosh naik Phone : 44032413 04.11.2018 11:39:05 UTC Sandipbhai Patel (QRSPB1) Reset the alarm at panel No alarm Exist at panel
90515539 | 2018-12-02 | A081-1SB220N2 | Lights are not working in AC area | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10278294 | 700002356603 | ABB MALAYSIA | Electrical | 36.9 | 4 | 4 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 19.10.2018 19:33:16 UTC Yuan Ferry Saputra (QRYSA1) Lights in train-1 AC area Post treatment string no. 2 <(>&<)> AC piperack corridor are not working, light bulb to be replaced. it may lead to trip hazzard during working <(>&<)> area rounding to due insufficient light 29.11.2018 06:17:41 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 F-LOC CHANGED TO A081-1SB220N2- LIGHTING
90515540 | 2018-12-02 | A081-1SB220N2 | Lights are not working in AC Finger-2 | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10278295 | 700002356603 | ABB MALAYSIA | Electrical | 36.9 | 4 | 4 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 19.10.2018 19:38:10 UTC Yuan Ferry Saputra (QRYSA1) Lights are not working in AC area reactors Finger two second floor. light bulb to be replace. it may lead to trip hazard during working <(>&<)> area rounding due to insufficient light 29.11.2018 06:18:35 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 F-LOC CHANGED TO A081-1SB220N2- LIGHTING
90515829 | 2018-10-28 | A081-2SB210N2 | CCO-2R-3029 FAULTY LIGHTING CIRCUIT | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10280076 | 700002373562 | ABB MALAYSIA | Electrical | 96.8 | 6 | 0 | end of life | end of life-400W SHOCK FAULTY | Lamps | Adjust / reset | 27.10.2018 05:53:45 UTC Michael I Dela Cruz (QRMDE6) Phone 44032804 Clear description of the problem. FAULTY LIGHTING CIRCUIT FOR 2R-3029 LOACATION FROM 1ST ELEV. TO TOP ELEV. REQUIRED FOR CCO ACTIVITY. 2SB210N2-Q16 NEED TO DO TROUBLE SHOOTING TO DISCONNECT/ISOLATE THE BRANCH CIRCUIT IN FIELD CAUSING THE TRIP. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-Disconnect X E-isolation Requester Name : MICHAEL Phone : 31548632 29.10.2018 11:29:13 UTC Sudheer Kumar Pendurthi (QRSPE6) WE CHECKED AND FOUND 2SB210N2-Q16 CIRCUIT L3 PHASE FEEDING LAMPS(400W) WAS FAULTY.NEED TO BE CHECK <(>&<)> REPLACE.WE DIS-CONNECTED L3 PHASE FROM MCB REMAINING CIRCUITS KEEP IN SERVICE. NOW OK NOTE; WE WILL CREATE NEW NOTIFICATION FOR 400W LAMP CHECKING
90516071 | 2018-11-25 | A081-1SB220N2 | TUBELIGHT NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10280217 | 700002356603 | ABB MALAYSIA | Electrical | 36.9 | 4 | 4 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 29.10.2018 01:27:19 UTC Jigneshkumar Ambalal Maru (QRJMA7) Clear description of the problem. AT RX-3 FOUTH EVEVATION ( HPNG FC-06 FLOOR ) TOWARDS SOUTH SIDE STIRCASE TWO TUBELIGHT IS NOT WORKING AND RAIN WATER ACCUMULATED IN COVER. PEFS: N/A Prioriteit: Additional mitigations : Requester Name : JIGNESH MARU Phone : 44032313
90516309 | 2021-03-29 | A081-1F5111 | 1F5111-HEAT SHIELD HOOK CRACK;REPLC-> | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10280336 | 700002348459 | KTI | Integrity | 1778.91 | 12 | 12 | Fouling | Fouling- | Other - please specify in text field | Replace | 30.10.2018 06:21:51 UTC Mohan Dattatray Patil (QRMPA4) Phone 55738740 1F-5111, B ROW HEAT SHIELD HOOK(GTL SIDE) IS OBSERVED/FOUND CRACKED DURING BURNER CLEANING ACTIVITY. THIS HOOK IS HOLDING LOAD OF ALL HEAT SHIELDS IN B ROW AND NEED TO REPLACE TO AVOID SUDDEN BREAKING OF IT AND THEN SLING CAN MAKE DAMAGE TO SHIELDS AS WELL AS CAN HARM PEOPLE WORKING IN THAT ROW DURING BURNER CLEANING ACTIVITY. PICTURE ATTACHED. 29.03.2021 10:00:31 UTC Mohan Dattatray Patil (QRMPA4) Phone 55738740 Turn buckle was found replaced in other WO number 90632839. That notification was raised after breaking of the Turn buckle while this notification was taised before braking of turn buckle.
90516434 | 2018-01-01 | A081-FIRE HYDRANT | SCE-FH539 MONITOR SEVERELY DAMAGED> | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10280487 |  |  |  | 26739.43 | 1024 | 2504 | Other - please specify in text field | Other - please specify in text field-Hit by bus | Other - please specify in text fields | Fix / Repair | 31.10.2018 13:08:06 UTC Leo Gaigher (QRLGA0) Clear description of the problem. On the 30th of October a bus collided with a firewater monitor FH539, causing severe damage to the monitor (see attached photo). FH539 is located in Road C opposite K7211. Find attached PEFS, location, photos and specification details. PEFS: T4057083RevA_F001 <(>&<)> T4094054RevE_F001 Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 01.11.2018 04:47:41 UTC Viresh Shah (QRVSH1) SCE IMPAIRED, TMOC BEING RAISED, TEMP MONITOR IN PLACE BY FIT TEAM. SCE NOT IMPAIRED AS ALTERNATE ARRANGEMENT IS BEING MADE BY FIT AS WELL AS GROUND LEVEL OTHER MONITORS ARE AVAILABLE TO FIGHT FIRE IN CASE HAPPENED
90517063 | 2018-12-10 | A081-0S8361A | RETA- MSDU CENTRIFUGE HIGH VIBRATION | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10280974 | 700001729713 |  | Rotating | 5013.47 | 366 | 179 | Normal Wear | Normal Wear- | Bearing | Replace | 07.11.2018 01:45:16 UTC Leo Miranda (QRLMI0) Clear description of the problem. HIGH VIBRATION OBSERVED IN MSDU CENTRIFUGE DURING START UP. AUTO GREASER ALSO GOT DETACHED, NEED TO BE FIXED BACK. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : LEO Phone : 44032215 08.11.2018 04:25:49 UTC "Lenin, " Senthamil (QRLSE0) Baskar, RE- Observation MSDU observation 1.,,Bearing hosing mounting bolts are found loose due to high vibration . Internal inspection to be carried out . Unbalance might have happened 2.,,Kindly execute process & electrical isolation for internal inspection and bearing replacement 3.,,Also observe that the auto greaser is not functioning for NDE , it indicates with the LED light ( Green -Working normal , Red- Need at tention , If no light - Drive might have not functioning - The details
90517214 | 2018-12-01 | A081-0S0143A | 0S-0143A FILTER REPLACEMENT REQUIRED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10281110 | 700002201324 | DKME | Integrity | 1761.8 | 27 | 46 |  |  |  |  | 08.11.2018 10:11:09 UTC Amit Gaur (QRAGA0) 0S-0143A filter element replacment required
90517245 | 2019-02-12 | A081-2A8324 | MAINT SUPPORT TO EMPTY OUT DAF PH2 | MX09 | M_X_X | Routine Wrk LvL 5 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10278549 | 700002297332 |  | Integrity | 62.43 | 298 | 298 | Other - please specify in text field | Other - please specify in text field-Operation request | Other - please specify in text field | Other - please specify in text field | 22.10.2018 11:30:28 UTC Raju Sutham (QRRSU3) Clear description of the problem. PHASE 2 FFU DAF DRAIN VALVE TO SLAUDG PIT VALVE IS PASSING, TO ATTEND THIS JOB WE HAVE TO EMPTY OUT FFU DAF WITH DIESEL PUMP CONNECTING WITH HOSE WHICH REQUIRED CRANE . MAINT TEAM SUPPORT REQUIRED TO SHIFT HOSES DIESEL PUMP AND CONNECT AND EMPTY OUT FFU DAF. PEFS: T-4.118.867 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. ETP TRAIN 2 WILL BE STOP TO DO THIS JOB Additional mitigations : X WPS/ Work instruction needed X Scaffold X Crane X LOTO/Spading X Spading X JHA needed Requester Name : RAJU
90517615 | 2018-12-11 | A081-1A8324 | MAINT SUPPORT TO EMPTY OUT FFU DAF | MX09 | M_X_X | Routine Wrk LvL 5 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10281585 | 700002348718 |  | Integrity | 1369.63 | 380 | 380 | Other - please specify in text field | Other - please specify in text field-operation requirement | Other - please specify in text fields | Other - please specify in text field | 14.11.2018 11:38:13 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. PHASE 1 FFU DAF SCRAPPER IS DAMAGE CONDITION , TO CHECK THIS SCRAPPER WE HAVE TO DRAIN THE FFU DAF AND TO DRAIN DAF REQUIED DIESEL PUMP WITH HOSE CONNETION, PEFS: Prioriteit: Additional mitigations : X WPS/ Work instruction needed X Scaffold X Crane Electrical tasks: X E-Disconnect X E-isolation X JHA needed X Turn around related Turn around reason : Requester Name : CIFAS
90517857 | 2018-12-01 | A081-1A8324 | DAF-1 SMALL WHEEL DAMAGED CONDITION | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10281810 | 700002348718 |  | Integrity | 855.93 | 11 | 11 |  | - | Steel construction / Stairs / Handrails | Replace | 17.11.2018 23:36:21 UTC Raju Sutham (QRRSU3) Clear description of the problem. TRAIN-1 DAF NON DRIVE END NEW BRIDGE ONE OF THE SMALL WHEEL PARTIALLY DAMAGED AND MOVING IN UNEVEN CONDITION.NEED TO ATTEND PEFS: T-4.118.864 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. IF THE WHEEL DAMAGED CANNOT POSSIBLE TO RUN THE BRIDGE AND PROCESS UPSET IN DOWNSTREAM Additional mitigations : Product information : Product left in equipment SOOTY WATER Expected amount : Requester Name : Raju.s Phone : 44032215
90517994 | 2019-02-05 | A081-294XA-50200-S | 2LPU/105/106/107 EHT FAULT;FREQ ALM; | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10281470 | 700002607282 |  | Instrumentation | 0 | 18 | 10 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault- | Heat Tracing | Field repair | 13.11.2018 07:26:05 UTC Gopinath Kokoori Vadakkethil (QRGVA2) 4B1 console elec tracing common fail alarm; this alarm is from 276QI10030/TX 3<(>&<)>4; LPU/105/106/107 - alarm belong to 2F7611 Need to attend
90518292 | 2019-01-28 | A081-2SB210N2 | BB AREA FAULTY LAMPS REPLACEMENT ACTIVIT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10281990 | 700002373562 | ABB MALAYSIA | Electrical | 2902.64 | 44 | 97 | end of life | end of life- | Lamps |  | 20.11.2018 12:31:19 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90508551)FOUND MANY LAMPS ARE NOT WORKING(AROUND 50 LIGHT FITTING LAPMS 2X36W)AND SEE ATTACHED DOCUMENT FOR REFERANCE. PEFS: NOTE; MOBILE SCAFFOLDING REQUIRED IN BELOW THE MAIN PIPERACK Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : SUDHEER Phone : 70483198 28.01.2019 13:40:16 UTC Sudheer Kumar Pendurthi (QRSPE6) We are completed which is accessible by A type ladder <(>&<)> mobile scaffolding,and some area's scaffolding abstractions is there in below piperack we cann't move the mobile scaffolding 28.01.2019 13:43:43 UTC Sudheer Kumar Pendurthi (QRSPE6) We have some spare lamps other then this reserved materials and we consumed this material so that we can close this WO.
90518298 | 2018-01-01 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10282022 | 700002200042 | DKME | Integrity | 20565.32 | 27 | 46 |  |  |  |  | 21.11.2018 00:38:07 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0163A filter element replacement due to pigging operation frequent choking PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate processing Additional mitigations : Electrical tasks: X E-isolation Requester Name : Balakrishna.Mijar Phone : 44032115
90518300 | 2018-01-01 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10282023 | 700002200043 | DKME | Integrity | 1572.79 | 27 | 46 |  |  |  |  | 21.11.2018 00:40:04 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0163B filter element replacement due to pigging operation frequent choking PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate processing Additional mitigations : Electrical tasks: X E-isolation Requester Name : Balakrishna.Mijar Phone : 44032115
90518301 | 2019-01-17 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10282017 | 700002200643 | DKME | Integrity | 1682.39 | 27 | 46 |  |  |  |  | 21.11.2018 00:30:18 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0123B filter element replacement due to pigging operation frequent choking PEFS: T-13.370.023 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate processing Additional mitigations : Electrical tasks: X E-isolation Requester Name : Balakrishna.Mijar Phone : 44032115
90518306 | 2019-01-17 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10282016 | 700002201322 | DKME | Integrity | 1676.1 | 27 | 46 |  |  |  |  | 21.11.2018 00:27:16 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0123A filter element replacement due to pigging operation frequent choking PEFS: T-13.370.023 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate processing Additional mitigations : Electrical tasks: X E-isolation Requester Name : Balakrishna.Mijar Phone : 44032115
90518307 | 2018-01-01 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10282019 | 700002201324 | DKME | Integrity | 1660.03 | 27 | 46 |  |  |  |  | 21.11.2018 00:33:50 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0143A filter element replacement due to pigging operation frequent choking PEFS: T-4.094.330 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate processing Additional mitigations : Electrical tasks: X E-isolation Requester Name : Balakrishna.Mijar Phone : 44032115
90518308 | 2018-12-05 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10282020 | 700002202402 | DKME | Integrity | 12465.88 | 27 | 46 |  |  |  |  | 21.11.2018 00:35:51 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0143B filter element replacement due to pigging operation frequent choking PEFS: T-4.094.330 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate processing Additional mitigations : Electrical tasks: X E-isolation Requester Name : Balakrishna.Mijar Phone : 44032115
90518314 | 2019-01-02 | A081-1S0241 | 1S-0241 FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10281996 | 700002354895 | JFC CORPORATION | Integrity | 1708.9 | 24 | 66 |  |  |  |  | 20.11.2018 13:14:04 UTC Edwin Reyes (QRERE0) Clear description of the problem. 1S-0241 shows high DP, filter need to be replaced PEFS: T-13.370.089 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Yes because 1S-0241 amine filtration is not 100% effective What actions did you already take to solve the problem, share information. Raised notification Additional mitigations : Requester Name : Edwin Reyes Phone : 44032111
90518415 | 2018-12-16 | A081-2SB200N2 | 2SB200N2-CKT-19 NEED TO TROUBLE SHOOTING | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10282103 | 700002373557 | ABB MALAYSIA | Electrical | 55.35 | 10 | 10 | end of life | end of life- | Lamps | Repair / correct | 21.11.2018 14:03:55 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90509289)FOUND MANY LAMPS ARE NOT WORKING.DUE TO CIRCUIT-19 WAS TRIPPED CONDITION.NEED TO TROUBLE SHOOT PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : SUDHEER Phone : 70483198
90518431 | 2019-02-04 | A081-2SB200N2 | BA AREA FAULTY LAMPS REPLACEMENT ACTIVIT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10282095 | 700002373557 | ABB MALAYSIA | Electrical | 2268.36 | 18 | 72 | end of life | end of life- | Lamps |  | 21.11.2018 13:09:24 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90509289)FOUND MANY LAMPS ARE NOT WORKING(AROUND 30 LIGHT FITTING LAPMS 2X36W)AND SEE ATTACHED DOCUMENT FOR REFERANCE. PEFS: NOTE; MOBILE SCAFFOLDING REQUIRED IN BELOW THE MAIN PIPERACK Prioriteit: Additional mitigations : X Use moveable platform or man lift Electrical tasks: X E-isolation Requester Name : SUDHEER Phone : 70483198 31.01.2019 12:30:41 UTC Sudheer Kumar Pendurthi (QRSPE6) We are completed which is accessible by A type ladder and mobile scaffolding
90518432 | 2019-01-31 | A081-2SB200N2 | BA AREA FAULTY LAMPS REPLACEMENT ACTIVIT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10282098 | 700002373557 | ABB MALAYSIA | Electrical | 1825.51 | 20 | 46 | end of life | end of life- | Lamps |  | 21.11.2018 13:20:11 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90509289)FOUND MANY LAMPS ARE NOT WORKING(AROUND 20 LIGHT FITTING LAPMS 2X36W)AND SEE ATTACHED DOCUMENT FOR REFERANCE. NOTE; NO NEED SCAFFOLDING WE WILL WORK WITH 'A' TYPE LADDER PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : SUDHEER Phone : 70483198 24.12.2018 08:02:50 UTC Mohammad Alam (QRMANR) material withdrawn <(>&<)> used in T1 activities. 31.01.2019 12:47:53 UTC Sudheer Kumar Pendurthi (QRSPE6) We are completed which is accessible by A type ladder and mobile scaffolding
90518569 | 2018-12-22 | A081-294XA-50200-S | 2ET-LPU 050 EHT FLT ALM;HVU2 RV** | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10282255 | 700002607282 |  | Instrumentation | 0 | 12 | 176 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault- | Electronic card | Other - please specify in text field | 23.11.2018 12:59:45 UTC Gopinath Kokoori Vadakkethil (QRGVA2) LPU 4B1 Panel- 294XA50200 Elec trcng comn fail ; 2ET-LPU 050, HVU RV strtucture, Changed mode from MAIN to RED, Now no alarm. Need to attend. 30.12.2018 08:20:41 UTC Premkumar Dayalan (QRPDA2) Phone 70480663 Checked found ECM was burnt, then Replaced ECM, checked working normal.
90518728 | 2018-12-08 | A081-0X0104 | 0X-0104 CONVEYOR TO BE CLEANED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10282202 | 700002206193 |  | Electrical | 91.45 | 6 | 12 | Preventive Maintenance Work | Preventive Maintenance Work-Proactive cleaning work | frame | Cleaned | 22.11.2018 13:38:45 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0X-0104 conveyor to be cleaned after Dr M filter new batch prepared PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. 0X-0104 overload and choke Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90518781 | 2019-02-03 | A081-1SB220N2 | AC-F1- R3 SOUTH STAIR CASE TUBE LIGHTS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10282348 | 700002356603 | ABB MALAYSIA | Electrical | 2758.78 | 18 | 23 | end of life | end of life- | Lamps |  | 25.11.2018 09:33:08 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER Ops/ WO# 90516071- ITS FOUND THAT AC/ SGP- R3 SOUTH SIDE STAIR CASE ALL FLOOR 18WATTS LIGHTS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. 1LFE220E1-02L317; 02L311; 02L308 - 18W LAMPS- 6 PCs 1LFE220N2-19L310; 19L106; 19L303 - 18W LAMPS- 6 PCs PEFS: - Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : SANISH PAUL PHONE : 44032804 24.12.2018 08:04:51 UTC Mohammad Alam (QRMANR) material withdrawn <(>&<)> used in T1 LES column <(>&<)> AC area
90519441 | 2018-12-23 | A081-1SB220N2 | Poor illumination in AC Area | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10282577 | 700002356603 | ABB MALAYSIA | Electrical | 145.2 | 8 | 10 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 27.11.2018 22:51:47 UTC Maheshkumar Balubhai Dhanani (QRMDH1) Clear description of the problem. Many of lights are not working in AC area.Some of them are as below mentioned locations: 1. AC Pipe rack 2. AC sub pipe rack near pr etreatment area. 3. At 1R-1115 3rd Floor. 4. At 1R-1117 2nd and 3rd Floor. It requires a survey of whole AC area by electrical tea and needs rectification. PEFS: NA Prioriteit: Additional mitigations : Requester Name : Mahesh Dhanani Phone : 44032313 20.12.2018 07:27:05 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 ALREADY OUTSTANDING WOs AVAILABLE- 90519760, 90519761, 90518781, 90519753 AND FOR FINGER-3 NEW NOTIFICATION CREATED 10284794 23.12.2018 08:47:59 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 EQUIPMENT CODE CHANGED TO 700002356603- A081-1SB220N2 23.12.2018 08:53:12 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 FOR FINFAN AND RV AREA NOTIFICATION CRETAED- 10284945
90519584 | 2018-12-17 | A081-0S0143B | 0S-0143B HC FILTER CHOKE | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283000 | 700002202402 | DKME | Integrity | 264.83 | 27 | 46 |  |  |  |  | 02.12.2018 19:19:30 UTC Sivakumar Manokaran (QRSMAA) 0S-0143B Hydro carbon filter DP is high need to replace the filter element.
90519753 | 2019-02-16 | A081-1SB220N2 | AC PIPERACK-MAIN CORRIDOR TUBELIGHTS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10283069 | 700002356603 | ABB MALAYSIA | Electrical | 7171.34 | 146.1 | 176.1 | end of life | end of life- | Lamps |  | 03.12.2018 12:06:40 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER Ops WO# 90515539- VISUAL INSPECTION DONE FOR PIPERACK MAIN CORRIDOR AREA/ POST TREATMENT AREA FOUND 200 PCs OF 36W TUBE LIGHTS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. PEFS:- Prioriteit: X- Movable Scaffolding required Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : SANISH PAUL PHONE : 44032804
90519760 | 2019-02-10 | A081-1SB220N2 | AC REACTOR AREA TUBELIGHTS FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10283070 | 700002356603 | ABB MALAYSIA | Electrical | 5538.95 | 63.2 | 66.2 | end of life | end of life- | Lamps | Replace | 03.12.2018 12:11:46 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER Ops WO# 90515539- VISUAL INSPECTION DONE FOR REATOR AREA GROUND FLOOR LEVEL, FOUND 30 PCs OF 36W TUBE LIGHTS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. PEFS:- Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : SANISH PAUL PHONE : 44032804 20.12.2018 13:30:05 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 ON 20-DEC-18- REACTORS AREA- 36W- 90 PCs AND 18W- 20 PCs OF LAMPS REPLACED, NEED TO CONTINUE
90519761 | 2018-12-27 | A081-1SB220N2 | AC FINGER-2 2nd FLOOR TUBELIGHTS FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10283072 | 700002356603 | ABB MALAYSIA | Electrical | 1327.22 | 44 | 77 | end of life | end of life- | Lamps | Replace | 03.12.2018 12:27:29 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER Ops/ WO# 90515540- VISUAL INSPECTION DONE FOR FINGER-2 SECOND FLOOR FLOOR LEVEL, FOUND 60 PCs OF 36W TUBE LIGHTS AND 20 PCs OF 18W TUBE LIGHTS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. PEFS:- Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : SANISH PAUL PHONE : 44032804
90520084 | 2018-01-01 | A081-0S0163A | OS-0163A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283544 | 700002200042 | DKME | Integrity | 167.8 | 27 | 46 |  |  |  |  | 06.12.2018 08:29:11 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0163A Filter element to be replaced after exhaustion.
90520085 | 2018-12-26 | A081-0S0163A | OS-0163A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283543 | 700002200042 | DKME | Integrity | 19141.97 | 27 | 46 |  |  |  |  | 06.12.2018 08:26:24 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0163A filter element to be replaced after exhaustion.
90520086 | 2018-12-20 | A081-0S0163B | OS-0163B FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283547 | 700002200043 | DKME | Integrity | 166.18 | 27 | 46 |  |  |  |  | 06.12.2018 08:35:30 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0163B filter element to be replaced after exhaustion.
90520089 | 2018-01-01 | A081-0S0163B | OS-0163B FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283545 | 700002200043 | DKME | Integrity | 7984 | 27 | 46 |  |  |  |  | 06.12.2018 08:32:25 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0163B filter element to be replaced after exhaustion.
90520090 | 2018-01-01 | A081-0S0123A | OS-0123A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283529 | 700002201322 | DKME | Integrity | 1404.42 | 27 | 46 |  |  |  |  | 06.12.2018 08:08:19 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0123A filter element to be replaced after exhaustion.
90520091 | 2019-11-18 | A081-0S0123A | OS-0123A FILTER ELEMENT TO BE REPLACED-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283542 | 700002201322 | DKME | Integrity | 3935.61 | 27 | 46 |  |  |  |  | 06.12.2018 08:23:02 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0123A filter element to be replaced after exhaustion.
90520092 | 2018-12-21 | A081-0S0143A | 0S-0143A FILTER REPLACEMEMNT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283519 | 700002201324 | DKME | Integrity | 18612.92 | 27 | 46 |  |  |  |  | 06.12.2018 07:34:14 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0143A filkter element to be replaced after exhaustion.
90520093 | 2018-12-20 | A081-0S0143A | 0S-143A FILTER TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283522 | 700002201324 | DKME | Integrity | 242.59 | 27 | 46 |  |  |  |  | 06.12.2018 07:36:09 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0143A filter element to be replaced after exhaustion.
90520094 | 2018-12-20 | A081-0S0143B | OS-0143B Fiter element to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283527 | 700002202402 | DKME | Integrity | 264.66 | 27 | 46 |  |  |  |  | 06.12.2018 07:56:20 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0143B Filter element to be replaced after exhaustion.
90520095 | 2018-12-20 | A081-0S0143B | OS-0143B FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10283528 | 700002202402 | DKME | Integrity | 303.45 | 27 | 46 |  |  |  |  | 06.12.2018 08:02:28 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) OS-0143B FILTER element to be replaced after exhaustion.
90520298 | 2019-01-03 | A081-1SB210N2 | 1R-3025 Top Manway Light not working | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10282597 | 700002352082 | ABB MALAYSIA | Electrical | 27.68 | 4 | 4 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 28.11.2018 04:38:16 UTC Chon Sung Ong (QRCON0) Clear description of the problem. 1R-3025 Top Man Way Fluorescent tube Light Not working. CCO Activity in progress. Light to be rectified. Buchen require this light during Loading activity PEFS: Prioriteit: Additional mitigations : Requester Name : Ong Chon Sung Phone : 28.11.2018 05:42:43 UTC Chon Sung Ong (QRCON0) Light Tag No. 1LFN210N215L114 03.01.2019 07:50:47 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 AREA INSPECTEDM G1 CREATED- 10285896
90520341 | 2018-12-09 | A081-2SB200N2 | PITSTOP-2K-3141 floor poor lighting | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10283697 | 700002373557 | ABB MALAYSIA | Electrical | 234.72 | 18 | 50 | end of life | end of life- | Lamps | Replace | 09.12.2018 06:33:56 UTC Rameshkumar Jadavji Kanani (QRRKA3) Clear description of the problem. 2K-3141 lighting is poor PEFS: Prioriteit: Additional mitigations : Requester Name : Ramesh Kanani Phone : 44032311
90520432 | 2019-11-12 | A081-0S8361A | RETA- 0SM8361A INTL INSPECT AND CLEANING | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10283224 | 700001729713 |  | Rotating | 164.78 | 16 | 25 | Product Contamination | Product Contamination- | Casing | Cleaned | 04.12.2018 12:38:27 UTC Eric Ates (QREAT0) Clear description of the problem. 0S8361A SLUDGE DEWATERING CENTRIFUGE POOR SLUDGE PRODUCTION SUSPECTED CHOKING INTERNALLY NEED TO INSPECT AND CLEAN PEFS: T-4.258.845 Prioriteit: Additional mitigations : X LOTO/Spading X Block and bleed Electrical tasks: X E-isolation X JHA needed Requester Name : DAVID Phone : 44032215 09.12.2018 07:21:07 UTC "Lenin, " Senthamil (QRLSE0) RE SUGESTED TO OPEN COVER AND INTERNAL INSPECTION AND CLEANING ICC REQUIRED
90520433 | 2019-01-19 | A081-0S8361A | LEAK, WAT, ROTA METER, FLOC, MSDU F03 | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10283778 | 700001729713 |  | Rotating | 48.68 | 54 | 50 | Normal Wear | Normal Wear- | Other - please specify in text field | Fix / Repair | 10.12.2018 01:39:22 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. MSDU flocculant preparation tank water flow Rota meter crack. Rota meter to be replaced PEFS: Prioriteit: Additional mitigations : X WPS/ Work instruction needed Electrical tasks: Requester Name : Bagus Phone : 44032215 23.01.2019 14:30:43 UTC Yogarajan Pandiyan (QRYPA0) Rotameter Cracks repaired by PGCC and lined up.
90520793 | 2018-12-16 | A081-1F5111 | 1/2F5111 IR SCANNING BY P&T;OPLN | MX04 | M_FUR_X | Schedule Breaker | 0 |  | SMR FURNACE | CM | LPU | 10283994 | 700002348459 | KTI | Integrity | 1391.28 | 210 | 649 | No feed | No feed-Periodic inspection purpose | Other - please specify in text field | Inspect | 13.12.2018 00:54:48 UTC Santosh Naik (QRSNA3) Clear description of the problem. 2F7611 HTF furnace IR scanning to be done. As requested by PS mail and SS. PEFS: T-4.101.279 Prioriteit: Additional mitigations : Requester Name : Jignesh Gohil Phone : 44032414 13.12.2018 04:45:44 UTC Vijay Paramasivam (QRVPA3) Phone 44032637 P&T is arriving on 16th OPS delayed info, SB created in line with OPS morning meeting agreement. 17.12.2018 15:21:46 UTC Velmurugan Subramanian (QRVSU0) In 1F5111 two inspection door found glass damaged.New glasses replaced Number 4 and 9 GTL side second floor.
90520945 | 2018-12-30 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10284226 | 700002202402 | DKME | Integrity | 265.73 | 27 | 46 |  |  |  |  | 16.12.2018 04:27:50 UTC Elangovan Muthusamy (QREMU0) 0S-143B dp high filter element to be replaced.
90520951 | 2018-12-30 | A081-2SB210N2 | 2SB210N2-33 (Q40) CKT TRIP NEED TO TEST | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10284010 | 700002373562 | ABB MALAYSIA | Electrical | 163.67 | 10 | 10 | Overload | Overload- | Fuse / MCB | Adjust / reset | 13.12.2018 05:13:14 UTC Mageshkumar Rajaram (QRMRA1) Phone 44032804 2804 Clear description of the problem. 2SB210N2-33 (Q40) CIRCUIT TRIPPED. TO BE CHECK THE CABLE <(>&<)> SOCKET OUTLETS PRIOR TO ENERGISE. (SOCKET OUTLETS FEEDING TO 2K-3041 COMPRESSOR SHED) PEFS: Prioriteit: Additional mitigations : Requester Name : MAGESHKUMAR RAJARAM Phone : 31548616
90521009 | 2019-02-03 | A081-0S0163A | 0S-163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10284258 | 700002200042 | DKME | Integrity | 13868.1 | 27 | 46 |  |  |  |  | 16.12.2018 10:30:07 UTC Elangovan Muthusamy (QREMU0) 0S-163A DP high filter element to be replaced.
90521011 | 2018-12-19 | A081-0S0163B | 0S-163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10284259 | 700002200043 | DKME | Integrity | 1544.14 | 27 | 46 |  |  |  |  | 16.12.2018 10:30:45 UTC Elangovan Muthusamy (QREMU0) 0S-163B DP high filter element to be replaced.
90521013 | 2018-01-01 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10284260 | 700002201324 | DKME | Integrity | 1654.47 | 27 | 46 |  |  |  |  | 16.12.2018 10:32:38 UTC Elangovan Muthusamy (QREMU0) 0S-143A DP high filter element to be replaced
90521014 | 2018-12-29 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10284261 | 700002202402 | DKME | Integrity | 226.02 | 27 | 46 |  |  |  |  | 16.12.2018 10:33:45 UTC Elangovan Muthusamy (QREMU0) 0S-143B DP high filter element to be replaced
90521724 | 2019-01-08 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10284793 | 700002201324 | DKME | Integrity | 244.72 | 7 | 46 |  |  |  |  | 20.12.2018 07:02:14 UTC Elangovan Muthusamy (QREMU0) 0S-143A dp high filter to be replaced.
90521794 | 2018-11-01 | A081-1SB220N2 | AC FINFAN/ RV AREA TUBELIGHTS FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10284945 | 700002356603 | ABB MALAYSIA | Electrical | 2935.33 | 84 | 85.2 | end of life | end of life- | Lamps | Replace | 23.12.2018 08:52:10 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER Ops/ WO# 90519441- VISUAL INSPECTION DONE FOR FINFAN AND RV AREA FOUND 120 PCs OF 36W TUBE LIGHTS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. PEFS:- Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : VEERRAJU PHONE : 44032804 30.01.2019 06:25:49 UTC Mohammad Alam (QRMANR) MATERIAL WITHDRAW AND USED TO T2 WO, HENTCE EXTRA MATERIAL RESERVED.
90521798 | 2019-03-13 | A081-1SB220N2 | AC FINGER-3 ALL FLOORS FAULTY TUBELIGHTS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10284794 | 700002356603 | ABB MALAYSIA | Electrical | 9074.23 | 136 | 212.1 | end of life | end of life- | Lamps |  | 20.12.2018 07:25:05 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER Ops/ WO# 90519441- VISUAL INSPECTION DONE FOR FINGER-3 ALL FLOOR LEVELS, FOUND 150 PCs OF 36W TUBE LIGHTS AND 120 PCs OF 18W TUBE LIGHTS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. PEFS:- Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : SANISH PAUL PHONE : 44032804
90522462 | 2019-02-03 | A081-294XA-50200-S | 2ET-LPU-084 NEW.EHT FLT;TAKN ON REDUNT** | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10285247 | 700002607282 |  | Instrumentation | 518.42 | 78 | 76 | Power / other utility failure | Power / other utility failure-Internal electronic circuit failure | Heat Tracing | Hardware Replacement | 27.12.2018 00:30:26 UTC Jayantilal Patel (QRJPA5) Clear description of the problem. 2ET LPU-084 - Electric heat tracing not working on Main mode giving fault alarm PEFS: Prioriteit: X Insulation Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : J R PATEL Phone : 44032413
90522478 | 2019-01-01 | A081-0S8361A | MSDU INSTRUMENT AIR SUPPLY FAILURE | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10285383 | 700001729713 |  | Rotating | 91.18 | 8 | 8 | Normal Wear | Normal Wear-Air leak from the tube fitting | Instrumentation | Fix / Repair | 28.12.2018 00:29:06 UTC Raju Sutham (QRRSU3) Clear description of the problem. MSDU INSTRUMENT AIR SUPPLY FAILURE OF VALVE M-401, FOUND SUPPLY LINE AIR IS PASSING PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. CANTRIFUGE CANNOT POSSIBLE TO RUN Additional mitigations : Requester Name : Raju.S Phone : 44032215
90522579 | 2019-02-10 | A081-1SB220N2 | AC-F2_1LFN220E105-L203 FITTING DAMAGED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10285457 | 700002356603 | ABB MALAYSIA | Electrical | 544.1 | 10 | 25 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace | 29.12.2018 05:50:58 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. DURING LAMP REPLACEMENT AT AC FINGER-2 AREA ITS FOUND THAT 36W TUBE LIGHT FITTING 1LFN220E105-L203 INTERNALLY DAMAGED AND NOT GLOWING, NEED TO REPLACED WITH NEW. PEFS: - Prioriteit: X- Scaffolding required Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : VEERRAJU PHONE : 44032804 20.01.2019 06:48:19 UTC Mohammad Alam (QRMANR) 36W TUBE NOT AVAILABLE,TUBE BOOKED OTHER WO.
90523034 | 2018-01-01 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10285805 | 700002200042 | DKME | Integrity | 0 | 27 | 46 |  |  |  |  | 02.01.2019 08:29:26 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. Condensate filter 0S-0163A filter element to be replacement - Pigging operation PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate couldn't process What actions did you already take to solve the problem, share information. if S/By filter to be taken online Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-isolation X Equipment with H2S Requester Name : Balakrishna.Mijar Phone : 44.32115
90523035 | 2018-01-01 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10285763 | 700002200043 | DKME | Integrity | 539 | 27 | 46 |  |  |  |  | 01.01.2019 13:46:24 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0163 B filter choked and filter element to be replaced PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. Filter change over done,0S-0163A in service Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-Disconnect X Equipment with H2S Requester Name : Balakrishna.Mijar Phone : 44032115
90523036 | 2019-01-28 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10285806 | 700002200043 | DKME | Integrity | 357.44 | 27 | 46 |  |  |  |  | 02.01.2019 08:31:52 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. Condensate filter 0S-0163B filter element to be replacement - Pigging operation PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate couldn't process What actions did you already take to solve the problem, share information. if S/By filter to be taken online Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-isolation X Equipment with H2S Requester Name : Balakrishna.Mijar Phone : 44.32115
90523037 | 2019-02-14 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10285807 | 700002200043 | DKME | Integrity | 12755.33 | 46 | 46 |  |  |  |  | 02.01.2019 08:37:01 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. Condensate filter 0S-0163B filter element to be replacement - Pigging operation PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate couldn't process What actions did you already take to solve the problem, share information. if S/By filter to be taken online Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-isolation X Equipment with H2S Requester Name : Balakrishna.Mijar Phone : 44.32115
90523038 | 2018-01-01 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10285802 | 700002201324 | DKME | Integrity | 12891.64 | 27 | 46 |  |  |  |  | 02.01.2019 08:21:19 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. Condensate filter 0S-0143A filter element to be replacement - Pigging operation PEFS: T-4.094.330 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate couldn't process What actions did you already take to solve the problem, share information. if S/By filter to be taken online Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-isolation X Equipment with H2S Requester Name : Balakrishna.Mijar Phone : 44.32115
90523310 | 2019-02-18 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10285803 | 700002202402 | DKME | Integrity | 1822.36 | 46 | 46 |  |  |  |  | 02.01.2019 08:24:52 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. Condensate filter 0S-0143B filter element to be replacement - Pigging operation PEFS: T-4.094.330 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate couldn't process What actions did you already take to solve the problem, share information. if S/By filter to be taken online Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-isolation X Equipment with H2S Requester Name : Balakrishna.Mijar Phone : 44.32115
90523311 | 2019-01-15 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10285804 | 700002202402 | DKME | Integrity | 202.97 | 27 | 46 |  |  |  |  | 02.01.2019 08:26:49 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. Condensate filter 0S-0143B filter element to be replacement - Pigging operation PEFS: T-4.094.330 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Condensate couldn't process What actions did you already take to solve the problem, share information. if S/By filter to be taken online Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-isolation X Equipment with H2S Requester Name : Balakrishna.Mijar Phone : 44.32115
90523780 | 2019-02-24 | A081-1SB210N2 | 1R-3025 TOP MANWAY BUSTED TUBELIGHTS | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10285896 | 700002352082 | ABB MALAYSIA | Electrical | 636.36 | 12 | 14.1 | end of life | end of life- | Lamps |  | 03.01.2019 07:47:07 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER OPS WO-90520298, VISUAL INSPECTION DONE AT 1R-3025 TOP MAN WAY AREA BUSTED TUBE LIGHTS TO BE REPLACED WITH NEW. 36W LAMPS REQUIRED- 20 PCs PEFS: - Prioriteit: X- "A" Ladder use Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : VASIM Phone : 44032804 30.01.2019 06:22:11 UTC Mohammad Alam (QRMANR) MATERIAL WITHDRAW AND USED TO T2 WO.HENCE EXTRA MATERIAL RESERVED.
90523835 | 2019-06-18 | A081-0S0163A | 0S-163 A Filter replacement. | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10286011 | 700002200042 | DKME | Integrity | 1617.05 | 27 | 46 |  |  |  |  | 03.01.2019 19:56:07 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163 A Filter need to be replaced after exhaustion. PEFS: T-4.094.342 Prioriteit: Additional mitigations : Requester Name : PRABU SANKAR Phone : 44032115
90523837 | 2019-06-19 | A081-0S0163B | 0S-163 B filter replacement. | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10286016 | 700002200043 | DKME | Integrity | 1547.54 | 27 | 46 |  |  |  |  | 03.01.2019 20:03:37 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) Clear description of the problem. 0S-163 B Filter need to be replaced after exhaustion. PEFS: T-4.094.342 Prioriteit: Additional mitigations : Requester Name : PRABU SANKAR Phone : 44032115
90523838 | 2019-04-13 | A081-0S0163B | 0S-163 B filter replacement. | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10286015 | 700002200043 | DKME | Integrity | 2109.39 | 27 | 46 |  |  |  |  | 03.01.2019 20:02:19 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) Clear description of the problem. 0S-163 B Filter need to be replaced after exhaustion. PEFS: T-4.094.342 Prioriteit: Additional mitigations : Requester Name : PRABU SANKAR Phone : 44032115
90523840 | 2019-06-17 | A081-0S0143A | 0S-143 A FILTER REPLACEMENT. | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10286010 | 700002201324 | DKME | Integrity | 10929.43 | 27 | 48 |  |  |  |  | 03.01.2019 19:53:23 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-143 A filter need to be replaced after exhaustion. PEFS NO; T-4.094.330
90523841 | 2019-04-29 | A081-0S0143B | 0S-143 B filter replacement | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10286012 | 700002202402 | DKME | Integrity | 1365.37 | 27 | 48 |  |  |  |  | 03.01.2019 19:58:54 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) Clear description of the problem. 0S-143 B Filter need to be replaced after exhaustion. PEFS: T-4.094.330 Prioriteit: Additional mitigations : Requester Name : PRABU SANKAR Phone : 44032115
90523842 | 2019-04-08 | A081-0S0143B | 0S-143 B filter replacement | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10286013 | 700002202402 | DKME | Integrity | 2062.2 | 27 | 48 |  |  |  |  | 03.01.2019 20:00:44 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) Clear description of the problem. 0S-143 B Filter need to be replaced after exhaustion. PEFS: T-4.094.330 Prioriteit: Additional mitigations : Requester Name : PRABU SANKAR Phone : 44032115
90525873 | 2019-03-31 | A081-0S0163B | 0S-0163B HC FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10287543 | 700002200043 | DKME | Integrity | 12053.11 | 27 | 46 |  |  |  |  | 17.01.2019 11:15:09 UTC Sivakumar Manokaran (QRSMAA) 0S-0163B HC filter DP high need to repalce the filter element replacement.
90525874 | 2019-03-05 | A081-0S0143A | 0S-0143A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10287544 | 700002201324 | DKME | Integrity | 1780.32 | 27 | 48 |  |  |  |  | 17.01.2019 11:17:49 UTC Sivakumar Manokaran (QRSMAA) 0S-0143A filter DP high need to repalce the filter element replacement
90525961 | 2019-01-17 | A081-0S0163A | 0s-0163A fHC filter DP high | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10287667 | 700002200042 | DKME | Integrity | 34.33 | 27 | 46 |  |  |  |  | 19.01.2019 20:14:06 UTC Sivakumar Manokaran (QRSMAA) 0S-0163A filter DP high need to replace the filter element.
90525962 | 2019-01-19 | A081-0S0143B | 0S-0143Bfilter DP high | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10287668 | 700002202402 | DKME | Integrity | 46.36 | 27 | 46 |  |  |  |  | 19.01.2019 20:15:44 UTC Sivakumar Manokaran (QRSMAA) 0S-0143B filter DP high need to replace the filter element
90525965 | 2019-02-21 | A081-0S0123A | 0s-0123A HC filter DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10287669 | 700002201322 | DKME | Integrity | 15395.5 | 27 | 46 |  |  |  |  | 19.01.2019 20:17:48 UTC Sivakumar Manokaran (QRSMAA) 0S-0123A Hydro carbon filter DP high need to repalce the filter element
90525985 | 2019-01-29 | A081-0P2021 | ACC cleaning pump 0P2021 phase 2 set up | MX09 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10287688 | 700002199414 | PRATISSOLI | Rotating | 1189.26 | 78 | 78 | Other - please specify in text field | Other - please specify in text field-operation requirement | Other - please specify in text field | Fix / Repair | 20.01.2019 05:57:38 UTC Baringin Simarmata (QRBSI0) Clear description of the problem. Set up ACC cleaning pump 0P2021 phase 2 and perform trial run PEFS: Prioriteit: Additional mitigations : Requester Name : Baringin Phone : 44032214 05.02.2019 03:32:41 UTC Sandeep Kumar (QRSKUQ) phase-2 set up done.job completed
90525986 | 2019-01-28 | A081-0P2021 | ACC cleaning pump 0P2021 phase 1 set up | MX09 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10287687 | 700002199414 | PRATISSOLI | Rotating | 496.98 | 78 | 78 | Other - please specify in text field | Other - please specify in text field-operation requirement | Other - please specify in text field | Fix / Repair | 20.01.2019 05:54:46 UTC Baringin Simarmata (QRBSI0) Clear description of the problem. Set up ACC cleaning pump 0P2021 phase 1 and perform trial run PEFS: Prioriteit: Additional mitigations : Requester Name : Baringin Phone : 44032214 03.02.2019 13:14:17 UTC Sandeep Kumar (QRSKUQ) acc cleaning set up done,3suction hoses and 4 discharge hoses connected ,job completed
90526008 | 2019-02-06 | A081-2SB210N2 | T-2 HPS-1 fixed plant light not working | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10286626 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 12 | 12 | end of life | end of life- | Lamps | Replace | 10.01.2019 23:06:40 UTC Nilotpal Mondal (QRNMO3) Clear description of the problem. TRAIN-2 , HPS -1ST STAGE AREA FIXED PLANT LIGHTING SURVEY DONE AND FOUND MANY LIGHTING ARE NOT WORKING. PLEASE REFFER THE ATTACHMENTS. SCAFFOLDING REQUIRE PEFS: Prioriteit: Additional mitigations : X Scaffold Requester Name : NILOTPAL MONDAL Phone : 44032311 28.01.2019 13:26:38 UTC Mohammad Alam (QRMANR) MATERIAL IN HAND 36W 02.02.2019 04:11:59 UTC Sudheer Kumar Pendurthi (QRSPE6) We are completed which is accessible by A type ladder and mobile scaffolding
90526009 | 2019-02-03 | A081-2SB200N2 | T-2 HPS-2 fixed plant light not working | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10286627 | 700002373557 | ABB MALAYSIA | Electrical | 555.04 | 12 | 36 | end of life | end of life- | Lamps |  | 10.01.2019 23:11:06 UTC Nilotpal Mondal (QRNMO3) Clear description of the problem. TRAIN-2 , HPS -2ND STAGE AREA FIXED PLANT LIGHTING SURVEY DONE AND FOUND MANY LIGHTING ARE NOT WORKING. PLEASE REFFER THE ATTACHMENTS. SCAFFOLDING REQUIRE PEFS: Prioriteit: Additional mitigations : X Scaffold Requester Name : NILOTPAL MONDAL Phone : 44032311 30.01.2019 06:15:50 UTC Mohammad Alam (QRMANR) MATERIAL WITHDRAW THROUGH T1 WO 02.02.2019 11:58:32 UTC Sudheer Kumar Pendurthi (QRSPE6) We are completed which is accessible by A type ladder and mobile scaffolding
90526074 | 2019-02-10 | A081-0X0104 | 0X-104 SCREW CONVEYOR CLEANING REQUIRED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10287716 | 700002206193 |  | Electrical | 182.93 | 9 | 12 | Other - please specify in text field | Other - please specify in text field-material fouling | conveyor | Cleaned | 20.01.2019 12:28:58 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) Clear description of the problem. 0X-104 Screw conveyor of Dr.M filter need to be cleaned on proactive basis. PEFS: T-13.370.060 Prioriteit: Additional mitigations : Requester Name : PRABU SANKAR Phone : 44032115
90526375 | 2019-02-23 | A081-1F5111 | 1/2F5111 IR RE-SCANNING,P&T;DEC18 | MX09 | M_FUR_X | Routine Wrk LvL 5 | 0 |  | SMR FURNACE | CM | LPU |  | 700002348459 | KTI | Integrity | 23901 | 1 | 1
90526377 | 2019-02-23 | A081-1F5111 | 1&2F5111TUBE TEMP HI;IR SCAN P&T;MX09 | MX09 | M_FUR_X | Routine Wrk LvL 5 | 0 |  | SMR FURNACE | CM | LPU |  | 700002348459 | KTI | Integrity | 26951 | 1 | 1
90526427 | 2019-02-26 | A081-FIRE HYDRANT | SCE FH442 1 x WINGED CAM ASSEMBLY SEIZED | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10288045 |  |  |  | 151.17 | 4 | 4 | Mechanical damage | Mechanical damage- | Other - please specify in text fields | Replace | 23.01.2019 11:36:53 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in January 2019 for FGP Train 1, it was found that the 1st (from left to right) 2.5" Winged Cam Assembly at hydrant FH442 was seized (see marked up attachment). FH442 is located in Road C-34 Tank OT - 0792. The spare part MM number is 10687723 Find attached PEFS, location, specification details. PEFS: T-4.352.430 <(>&<)> T4094056RevE_F001(location) Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90526430 | 2019-03-31 | A081-FIRE HYDRANT | SCE FH582 6" BUTTERFLY VALVE SEIZED-> | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10288048 |  |  |  | 1018.7 | 8 | 19 | Product Contamination | Product Contamination- | valve | Replace | 23.01.2019 11:54:06 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in January 2019 for FGP Train 1, it was found that the 6" Wafer Lugged Butterfly Valve at hydrant FH582 was seized (see marked up attachment). FH582 is in Road C-32 opposite Furnace. The spare part MM number is 10687722 Find attached PEFS, location, specification details. PEFS: T-4.352.430 <(>&<)> T4094053RevE_F001c (2) (location) Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90526434 | 2019-03-01 | A081-FIRE HYDRANT | SCE FH440 6" BUTTERFLY VALVE SEIZED | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10288042 |  |  |  | 913.36 | 8 | 19 | Mechanical damage | Mechanical damage- | Valves | Replace | 23.01.2019 11:24:01 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in January 2019 for FGP Train 1, it was found that the 6" Wafer Lugged Butterfly Valve at hydrant FH440 was seized (see marked up attachment). FH440 is located in Road C opposite main structure. The spare part MM number is 10687722. Find attached PEFS, location, specification details. PEFS: T-4.352.430 <(>&<)> T4094056RevE_F001(location) Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90526438 | 2019-02-24 | A081-FIRE HYDRANT | SCE FH443 2xWINGED CAM ASSEMBLIES FAULTY | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10288046 |  |  |  | 210.87 | 6 | 6 | Mechanical damage | Mechanical damage- | Other - please specify in text fields | Replace | 23.01.2019 11:44:09 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in January 2019 for FGP Train 1, it was found that the 2nd and 4th (from left to right) 2.5" Winged Cam Assemblies at hydrant FH443 were faulty (see marked up attachment). FH443 is located in Road C-34 Tank OT - 0791. The spare part MM number is 10687723 Find attached PEFS, location, specification details. PEFS: T-4.352.430 <(>&<)> T4094056RevE_F001(location) Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90527702 | 2019-02-18 | A081-0S8361A | FS-MSDU FLUSH VALVE INSTRUMENT AIR LOW | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10289054 | 700001729713 |  | Rotating | 50.27 | 6 | 0 | Preventive Maintenance Work | Preventive Maintenance Work-Air leak from fitting | Instrumentation | Fix / Repair | 03.02.2019 13:24:33 UTC Joyabrata Gupta (QRJGU0) Clear description of the problem. MSDU FLUSH VALVE 401 INSTRUMENT AIR PRESSURE SUPPLY LOW. FREQUENTLY TRIPPING THE UNIT. PEFS: Prioriteit: Additional mitigations : Requester Name : Phone :
90527945 | 2019-03-03 | A081-1F5111 | 1F5111 QP STACK FLUE GAS SAMPLING;MARCH | MX09 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10289250 | 700002348459 | KTI | Integrity | 0 | 36 | 39 | Other - please specify in text field | Other - please specify in text field-No Problem | Stack | Test | 05.02.2019 11:37:02 UTC Muthu Siva Krishnan Kalyani Rao (QRMKA2) 1F-5111 AMMONIA SLIP TEST FROM STACK 06.02.2019 05:01:55 UTC Vijay Paramasivam (QRVPA3) Phone 44032637 1F5111 QP STACK FLUE GAS SAMPLING FROM AH16 NOX SAMPLING
90527970 | 2019-02-07 | A081-0P2021 | RECTIFY 0P2021 ELECTRICAL PROBLEM | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10289310 | 700002199414 | PRATISSOLI | Rotating | 344.12 | 8 | 0 | Other - please specify in text field | Other - please specify in text field-Fuse blown high during starting | Other - please specify in text field | Fix / Repair | 06.02.2019 06:11:17 UTC Donald Enriquez (QRDEN0) Clear description of the problem. ACC Cleaning Skid pump 0P2021 not able to start due to Electrical Problem. To be checked and rectify the problem. PEFS: Prioriteit: Additional mitigations : Requester Name : Donald Phone : 44032213 07.02.2019 14:09:46 UTC Mutharasu Subbaih (QRMSU8) Checked and found L1 phase was blown out and the same was replaced by new one (50A,gG) normalised back now running normal.
90527995 | 2019-02-07 | A081-0P2021 | LEAK WAT ACC CLEANING PUMP SUCTION PH 2 | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10289331 | 700002199414 | PRATISSOLI | Rotating | 13888.87 | 56 | 56 | Normal Wear | Normal Wear- | Other - please specify in text field | Fix / Repair | 06.02.2019 08:23:44 UTC Donald Enriquez (QRDEN0) Clear description of the problem. ASU3 ACC cleaning skid pump 0P2021 suction line is having leak. To be checked and fix the problem PEFS: Prioriteit: Additional mitigations : Requester Name : Donald Phone : 44032213
90528282 | 2018-01-01 | A081-0S0123B | 0S-123B Filter DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289469 | 700002200643 | DKME | Integrity | 351.81 | 46 | 46 |  |  |  |  | 07.02.2019 22:18:02 UTC Elangovan Muthusamy (QREMU0) 0S-123B Filter DP high filter element to be replaced.
90528283 | 2019-06-01 | A081-0S0123B | 0S-0123B FILTER DP HIGH-> | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289468 | 700002200643 | DKME | Integrity | 12739.77 | 27 | 46 |  |  |  |  | 07.02.2019 22:17:13 UTC Elangovan Muthusamy (QREMU0) 0S-123B Filter DP high filter element to be replaced.
90528284 | 2019-11-24 | A081-0S0123B | 0S-0123B FILTER DP HIGH-> | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289466 | 700002200643 | DKME | Integrity | 4093.87 | 27 | 46 |  |  |  |  | 07.02.2019 22:13:51 UTC Elangovan Muthusamy (QREMU0) 0S-123A Filter DP high filter element to be replaced. 10.02.2019 06:19:53 UTC Justin Joseph Kachappilly (QRJKA1) 0S-0123B Filter element to be replaced
90528285 | 2020-02-01 | A081-0S0123B | 0S-0123B FILTER DP HIGH-> | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289467 | 700002200643 | DKME | Integrity | 8787.47 | 27 | 46 |  |  |  |  | 07.02.2019 22:15:27 UTC Elangovan Muthusamy (QREMU0) 0S-123A Filter DP high filter element to be replaced. 10.02.2019 06:21:54 UTC Justin Joseph Kachappilly (QRJKA1) 0S-0123B Filter element to be replaced
90528286 | 2019-03-18 | A081-0S0163A | 0S-163A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289477 | 700002200042 | DKME | Integrity | 389.57 | 27 | 46 |  |  |  |  | 07.02.2019 22:31:08 UTC Elangovan Muthusamy (QREMU0) 0S-163B Filter DP high filter element to be replaced. 10.02.2019 06:24:10 UTC Justin Joseph Kachappilly (QRJKA1) 0S-0163A Filter element to be replaced
90528287 | 2019-04-02 | A081-0S0163A | 0S-0163A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289474 | 700002200042 | DKME | Integrity | 22030.2 | 27 | 46 |  |  |  |  | 07.02.2019 22:27:17 UTC Elangovan Muthusamy (QREMU0) 0S-163A Filter DP high filter element to be replaced.
90528288 | 2019-04-19 | A081-0S0163A | 0S-0163A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289475 | 700002200042 | DKME | Integrity | 1589.84 | 27 | 46 |  |  |  |  | 07.02.2019 22:28:42 UTC Elangovan Muthusamy (QREMU0) 0S-163A Filter DP high filter element to be replaced.
90528289 | 2019-04-10 | A081-0S0163B | 0S-163B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289476 | 700002200043 | DKME | Integrity | 1797.21 | 27 | 46 |  |  |  |  | 07.02.2019 22:29:58 UTC Elangovan Muthusamy (QREMU0) 0S-163B Filter DP high filter element to be replaced.
90528290 | 2019-04-03 | A081-0S0143A | 0S-0143A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289471 | 700002201324 | DKME | Integrity | 2645.13 | 27 | 46 |  |  |  |  | 07.02.2019 22:22:45 UTC Elangovan Muthusamy (QREMU0) 0S-143A Filter DP high filter element to be replaced.
90528291 | 2019-04-20 | A081-0S0143A | 0S-0143A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289470 | 700002201324 | DKME | Integrity | 1695.13 | 27 | 46 |  |  |  |  | 07.02.2019 22:22:08 UTC Elangovan Muthusamy (QREMU0) 0S-143A Filter DP high filter element to be replaced.
90528292 | 2019-01-01 | A081-0S0143A | 0S-0143A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289472 | 700002201324 | DKME | Integrity | 7084.05 | 27 | 46 |  |  |  |  | 07.02.2019 22:24:47 UTC Elangovan Muthusamy (QREMU0) 0S-143B Filter DP high filter element to be replaced. 10.02.2019 06:28:38 UTC Justin Joseph Kachappilly (QRJKA1) 0S-0143A Filter element to be replaced
90528293 | 2019-03-30 | A081-0S0143B | 0S-0143B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10289473 | 700002202402 | DKME | Integrity | 1777.66 | 27 | 46 |  |  |  |  | 07.02.2019 22:25:58 UTC Elangovan Muthusamy (QREMU0) 0S-143B Filter DP high filter element to be replaced.
90529412 | 2019-03-20 | A081-2A8324 | DAF 2 SCRAPPER L SUPPORT CLAMP MISSING | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10289987 | 700002297332 |  | Integrity | 109.26 | 256 | 256 |  |  |  |  | 13.02.2019 22:08:16 UTC Joyabrata Gupta (QRJGU0) Clear description of the problem. IN ETP DAF TRAIN 2 BRIDGE SCRAPPER ONE L SUPPORTBOTTOM 2 CLAMPS ARE MISSING AND THE L SUPPORT IS HANGING FROM TOP CLAMP ONLY. PLEASE SEE THE ATTACHED PHOTO PEFS: T-4.118.867 Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation Requester Name : J.GUPTA Phone : 44032215 16.03.2019 11:23:05 UTC Tites Peter (QRTPE0) 4Numbers clamps fixed. Job completed.
90529413 | 2019-03-16 | A081-1A8324 | DAF-1 SCRAPPER SCUM BOARD L ARM DAMAGED | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10289823 | 700002348718 |  | Integrity | 661.69 | 209 | 209 | Normal Wear | Normal Wear- | Bolting and Gaskets | Fix / Repair | 11.02.2019 14:15:48 UTC Raju Sutham (QRRSU3) Clear description of the problem. TRAIN-1 DAF SCRAPPER SCUM BOARD SUPPORT L ROD DAMAGED CONDITION, NEED TO FIX, SUPPORT ROD ALREADY REMOVED TO AVOID FURTHER DAMAGED PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : Raju.s Phone : 44032212
90529513 | 2019-02-19 | A081-0S8361A | SDU CENTRIFUGE A MOTOR CMMND DISAGREE | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10290395 | 700001730109 | ABB | Electrical | 96.45 | 24 | 20 | Human Error | Human Error- | Control Circuit | Adjust / reset | 18.02.2019 10:53:28 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. SDU CENTRIFUGE A BOWL MOTOR COMMAND DISAGREE TO ATTEND PEFS: T-4.258.845 Prioriteit: Additional mitigations : Requester Name : CIFAS Phone : 44032215 19.02.2019 12:00:31 UTC V. Velyogeeswaran (QRVVE2) Phone 4403 2795 Found the drive control selection in HMI has been LOCAL mode instead of EXTERNAL CONTROL,then changed to EXTERNAL CONTROL mode,trial taken,ok
90529854 | 2019-03-23 | A081-1SB220N2 | AC 1LFN220N214L330 400W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10290372 | 700002356603 | ABB MALAYSIA | Electrical | 103.37 | 8 | 26 | end of life | end of life- | Lamps | Replace | 18.02.2019 07:16:27 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER PM WO# 90509879 AC/ SGP AREA - FOUND 1LFN220N214L330- 400WATTS LAMP FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. PEFS: - Prioriteit: X- Scaffolding required Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : VASIM PHONE : 44032804
90530756 | 2019-03-12 | A081-1SB210N2 | 1SB210N2-Q51/Q53 FAULTY LIGHTING CIRCUIT | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10291070 | 700002352082 | ABB MALAYSIA | Electrical | 158.01 | 10 | 10 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 25.02.2019 14:58:19 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. AS PER PM WO# 90509881- AB / HPS-1 AREA -FAULTY LIGHTING CIRCUITS NEAR REACTOR'S TOPSIDE PLATFORM FOUND 1SB210N2-Q51(CIRCUIT-40) <(>&<)> 1SB210N2-Q53(CIRCUIT-42) BREAKER TRIPPED CONDITION.NEED TO DO TROUBLE SHOOTING TO DISCONNECT/ISOLATE THE BRANCH CIRCUIT IN FIELD CAUSING THE TRIP. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : SUDHEER Phone :70483198 04.03.2019 12:23:16 UTC Sudheer Kumar Pendurthi (QRSPE6) 1)DURING TROUBLE SHOOTING WE FOUND 1LFN210N240L201 BALLAST/IGNIATOR WAS FAULTY AND DIS-CONNECTED CIRCUIT-40/L2 PHASE FROM SUBSTATION THEN RESETED REMAINING CIRCUITS ARE OK.NEED SCAFFOLDING FOR THIS ACTIVITY. 2)DURING TROUBLE SHOOTING WE FOUND 1LFN210N242L304 BALLAST/IGNIATOR WAS FAULTY AND DIS-CONNECTED LAMP SUPPLY FROM LAMP.THEN RESETED REMAINING CIRCUITS ARE OK.NEED SCAFFOLDING FOR THIS ACTIVITY.AND WE WILL CREATE SEPARATE NOTIFICATION FOR THIS ACTIVITY.
90530757 | 2019-04-10 | A081-1SB210N2 | AB_PIPERACK & FINFAN PLATFORM TUBELIGHTS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10291071 | 700002352082 | ABB MALAYSIA | Electrical | 5809.29 | 100 | 86 | end of life | end of life- | Lamps | Replace | 25.02.2019 15:04:43 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. AS PER PM WO# 90509881- AB / HPS-1 AREA - VISUAL INSPECTION DONE FOR PIPERACK MAIN CORRIDOR AREA / FINFAN PLATFORM AREA FOUND 300 PCs OF 36W TUBE LIGHTS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. PEFS: Prioriteit: Additional mitigations : X Scaffold (MOBILE SCAFFOLDING REQUIRED) Electrical tasks: X E-isolation X JHA needed Requester Name : SUDHEER Phone :70483198
90530758 | 2019-04-21 | A081-1SB210N2 | AB_REACTORS, EXCHANGERS AREA TUBELIGHTS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10291072 | 700002352082 | ABB MALAYSIA | Electrical | 6816.95 | 115 | 47.1 | end of life | end of life- | Lamps |  | 25.02.2019 15:14:05 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. AS PER PM WO# 90509881- AB / HPS-1 AREA - VISUAL INSPECTION DONE FOR U13000 REACTORS AREA AND EXCHANGERS AREA <(>&<)> COMPRESSOR AREA and U13400 FOUND 150 PCs OF 36W and 100 PCs 18W TUBE LIGHTS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. PEFS: Prioriteit: Additional mitigations : X Scaffold ("A" TYPE LADDER) Electrical tasks: X E-isolation X JHA needed Requester Name : SUDHEER Phone :70483198
90530762 | 2019-03-23 | A081-1SB220N2 | AC AREA LIGHT NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10290961 | 700002356603 | ABB MALAYSIA | Electrical | 145.21 | 8 | 8 | Internal failure / short | Internal failure / short- | Lamps | Adjust / reset | 24.02.2019 08:55:04 UTC Manjit Singh (QRMSI1) Clear description of the problem. In AC area eletrical light is poor near 1T1201 and 1E1216A/B need to check for other locations as reported by night shift D group PEFS: Prioriteit: Additional mitigations : Requester Name : Manjit singh
90530912 | 2019-02-27 | A081-1A8324 | DAF1 SCUM BOARD L-ANGLE SUPPORT DETACHED | MX04 | M_X_X | Emergency | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10291158 | 700002348718 |  | Integrity | 347.7 | 48 | 48 | accidental damage | accidental damage- | Other - please specify in text field | Other - please specify in text field | 27.02.2019 01:32:30 UTC Leo Miranda (QRLMI0) Clear description of the problem. TRAIN 1 DAF SCRAPER ONE OF THREE L-ARMS GOT DETACHED. SCUM BOARD POSITION LOWERED HENCE POTENTIAL TO GET ENTANGLED WITH THE SCUM TROUGH. PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. SUSPENDED SOLID REMOVAL BECAME INEFFICIENT DUE TO STOPPAGE OF CHEMICAL DOSING. SLUDGE WASTING IS ALSO REDUCED DUE TO THE OUTAGE OF THE SCRAPER. SCRAPER STOPPED AT ENTRY POSITION FOR EASY ACCESS AND READY FOR MAINTENANCE. Additional mitigations : X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : LEO Phone: 44032215
90531587 | 2019-05-12 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX04 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10291388 | 700002202402 | DKME | Integrity | 17850.64 | 27 | 48 |  |  |  |  | 01.03.2019 22:28:18 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0143B FILTER ELEMENT TO BE REPLACE PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. CONDENSATE PROCESSING What actions did you already take to solve the problem, share information. S/BY FILTER 0S-0143A ON LINE Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90532187 | 2019-07-24 | A081-2A8324 | TR2 DAF SCRAPPER MOTOR COVER DAMAGE FO1 | MX04 | E_MOT_LV | Routine Wrk Lvl 4 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10291789 | 700002297890 | ABB | Electrical | 650.79 | 12 | 33 | Premature failure | Premature failure- | Motor body including fancover | Replace | 06.03.2019 08:49:16 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. TR2 DAF Scrapper motor top cover damage, to be replaced as per Maintenance engineer area. PEFS: T-4.118.867 Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation Requester Name : Bagus Phone : 44032215
90532589 | 2019-03-14 | A081-0X0104 | 0X-104 VIEW GLASS CRACK TO BE REPLACED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10292018 | 700002206193 |  | Electrical | 0 | 0 | 12 |  |  |  |  | 09.03.2019 13:39:39 UTC Elangovan Muthusamy (QREMU0) 0X-104 screw conceyor view glass crack while loading bag, to be replaced.
90532590 | 2019-03-18 | A081-0X0104 | 0X-104 SCREW CONVEYOR TO BE CLEANED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10292020 | 700002206193 |  | Electrical | 0 | 6 | 12 | Fouling | Fouling- | Casing | Cleaned | 09.03.2019 13:42:36 UTC Elangovan Muthusamy (QREMU0) 0X-104 screw conveyor to be cleaned
90533860 | 2019-04-09 | A081-1F5111 | HW-1F-5111 B1 BURNER HEAD CRACK;REPLACE | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10292706 | 700002348459 | KTI | Integrity | 1635.68 | 58 | 125 | Normal Wear | Normal Wear-burner tip crack | Other - please specify in text field | Replace | 18.03.2019 07:26:42 UTC Sivakumar Dhandapani (QRSDH1) Clear description of the problem. 1F-5111 B1 BURNER HEAD CRACK OBSERVED DURING BURNER CLEANING ACTIVITY. IT IS REQUIRED TO REPLACE THE CRAKED BURNER HEAD BY CUT <(>&<)> TACK WELDING. SANPS ATTACHED. PEFS: Prioriteit: Additional mitigations : X JHA needed Requester Name : SIVAKUMAR Phone : 66208823
90533893 | 2019-04-11 | A081-0X0104 | 0X-104 SCREW CONVEYOR CLEANING REQUIRED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 4 | 0 |  | SCREW CONVEYOR | CM | FGP | 10292785 | 700002206193 |  | Electrical | 129.89 | 6 | 12 | Fouling | Fouling-Proactive cleaning work | rollers | Cleaned | 19.03.2019 03:37:51 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0X-104 screw conveyor of Dr.M filter need to be cleaned after every batch preparation proactively to avoid damage to glass cover. PEFS--T-4.262.215
90534335 | 2019-08-07 | A081-0S0123A | 0S-0123A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10293053 | 700002201322 | DKME | Integrity | 17981.46 | 27 | 46 |  |  |  |  | 21.03.2019 21:36:27 UTC Elangovan Muthusamy (QREMU0) 0S-123A DP high filter to be replaced.
90534383 | 2019-04-07 | A081-FIRE HYDRANT | SCE FH94 Stortz cap seized | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10293020 |  |  |  | 328.1 | 4 | 4 | Rust and dirt | Rust and dirt- | Other - please specify in text field | Replace | 21.03.2019 11:10:34 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in March 2019 for S<(>&<)>P, it was found that at hydrant FH94 the STORZ BLIND CAP ,40249537, AWGFTNG, was seized (see marked up attachments). FH94 is located in 4the Ave near OK 6751 Heater. The spare part MM number is 10684883. Leo Gaigher also has spare caps if required. Maintenance to contact Leo Gaigher QRLGA0. Find attached PEFS, location, specification details. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 08.04.2019 15:19:28 UTC Sandeep Kumar (QRSKUQ) cap replaced with new one,job completed
90534384 | 2019-04-07 | A081-FIRE HYDRANT | SCE FH95 Winged Cam Missing | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10293019 |  |  |  | 131.39 | 8 | 8 | Rust and dirt | Rust and dirt- | Other - please specify in text field | Replace | 21.03.2019 11:06:46 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in March 2019 for S<(>&<)>P, it was found that at hydrant FH95 the 4th Winged Cam Assembly Kit (from left to right) was missing (see marked up attachments). FH95 is located in 4th Ave near OGT 6731. The spare part MM number is 10687723. Leo Gaigher has picked up the winged cam assembly in the area, it might just need to be refastened. Maintenance to contact Leo Gaigher QRLGA0. Find attached PEFS, location, specification details. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 08.04.2019 15:26:13 UTC Sandeep Kumar (QRSKUQ) new winged cam assembly installed,job completed
90534385 | 2019-04-07 | A081-FIRE HYDRANT | SCE FH87 Winged cam missing | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10293017 |  |  |  | 131.4 | 4 | 4 | Rust and dirt | Rust and dirt- | Other - please specify in text field | Fix / Repair | 21.03.2019 11:02:00 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in March 2019 for S<(>&<)>P, it was found that at hydrant FH87 the 4th Winged Cam Assembly Kit (from left to right) was missing (see marked up attachments). FH87 is located in 3rd Ave near OGT 6741. The spare part MM number is 10687723. Leo Gaigher has picked up the winged cam assembly in the area, it might just need to be refastened. Maintenance to contact Leo Gaigher QRLGA0 Find attached PEFS, location, specification details. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 08.04.2019 15:35:45 UTC Sandeep Kumar (QRSKUQ) new winged cam assembly installed,job completed
90534475 | 2019-04-07 | A081-1A8324 | REMOVAL OF DIESEL PUMP IN T2 SUF AREA | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10293263 | 700002348718 |  | Integrity | 301.59 | 121 | 121 | Other - please specify in text field | Other - please specify in text field-operation requirement | Other - please specify in text field | Other - please specify in text field | 25.03.2019 01:02:25 UTC Leo Miranda (QRLMI0) Clear description of the problem. DIESEL PUMP USED TO EMPTY OUT DAF 1 FLOTATION TANK NEED TO BE REMOVED FROM THE AREA AND TO BE SHIFTED BACK NEAR THE CDF AREA. PEFS: Prioriteit: Additional mitigations : X Crane BOOM TRUCK REQUIRED TO LIFT AND TRANSPORT THE DIESEL PUMP TO THE NEXT LOCATION. Requester Name: LEO Phone: 44032215
90534555 | 2019-04-04 | A081-0P2021 | ASU8 ACC CLNG PUMP DISCH CRACK (WELD) | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10293288 | 700002199414 | PRATISSOLI | Rotating | 1731.95 | 89 | 79 | Normal Wear | Normal Wear- | Other - please specify in text field | Replace | 25.03.2019 06:41:16 UTC Mohamed Yunus (QRMLI1) Clear description of the problem. ASU 8 ACC CLEANING PUMP RECYCLE LINE SPOOL WELDING LEAK. CHECK AND RECTIFY. ALSO FIX LEAK AT TRANSMITTER SPOOL JOINT. PEFS: Prioriteit: Additional mitigations : Requester Name : YUNUS Phone : 2214
90538166 | 2019-05-08 | A081-1SB220N2 | 1E-8401,1E-8402,Finfan Area light off. | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10293683 | 700002356603 | ABB MALAYSIA | Electrical | 76.57 | 12 | 10 | end of life | end of life- | Lamps | Replace | 30.03.2019 00:04:46 UTC Kamalkumar Shukla (QRKSH1) Clear description of the problem. 1E-8401,1E-8402,Finfan Area Poor lighting we need this area normal lighting. we have to check temporary clamp provided at 1E-8402 O/L line as well as 1E-8401 lines as per PSF5 walk the line. Light Nos. are 1LNF220N220N214L132,1LNF220N220N214L224,1LNF220N220N214L222 ,1LNF220N220N214L225,1LNF220N220N214L324,1LNF220N220N214L312 ,1LNF220N220N214L315,etc Prioriteit: Additional mitigations : Requester Name : Kamalkumar.Shukla Phone : 44032313
90538619 | 2019-06-27 | A081-1SB220N2 | PM_FLT_LIGHT FITITING DIFFUSERS DAMAGED | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10294153 | 700002356603 | ABB MALAYSIA | Electrical | 15591.54 | 118 | 110 | Mechanical damage | Mechanical damage- | Lighting Fixture |  | 04.04.2019 05:36:49 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER PM WO# 90531761, VISUAL INSPECTION MADE AND REFER FOR OBSERVATION IN ATTACHED QAQC, EX INTEGRITY RELATED SYMPTOMS. 18W DIFFUSER FAILED- 5 PCs TO BE REPLACED 36W DIFFUSER FAILED- 65 PCs TO BE REPLACED PEFS:- Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : VASIM PHONE : 44032804 08.04.2019 08:16:40 UTC Mohammad Alam (QRMANR) DIFFUSER STOCK NOT AVAILABLE <(>&<)> ETA IS JUNE 2019.
90538699 | 2019-04-15 | A081-0S8361A | FS- MSDU CENTRIFUGE MOTOR FAULT- F03 | MX04 | E_MOT_LV | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10294307 | 700001730110 | ABB | Electrical | 551.05 | 52 | 76 | Software / Hardware fault | Software / Hardware fault-Chance of control board fault | Control Circuit | Check/ Inspect/ Test | 07.04.2019 04:54:00 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. MSDU centrifuge motor having motor fault, please reset to run the unit to maintain the healthiness of the plant and maintain the plant throughput PEFS: Prioriteit: Additional mitigations : Electrical tasks: Requester Name : Bagus Phone : 44032215
90538997 | 2019-12-23 | A081-1F5111 | HW-1F5111-REPLACE CRACKED G8 BURNER HEAD | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10293790 | 700002348459 | KTI | Integrity | 1369.8 | 44 | 125 | Coking | Coking- | Burner - cup throat | Inspect | 31.03.2019 11:58:05 UTC Pranab Ghorui (QRPGH0) FOUND CRACKED OF BURNER HEAD DURING BURNER CLEANING ACTIVITY OF G8 BURNER. NEED TO REPLACE THE BURNER HEAD WITH NEW ONE.
90539080 | 2019-05-21 | A081-0S8361A | SDU A CENTRATE LIQUIR BELLOW DAMAGE | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10294545 | 700001729713 |  | Rotating | 5309.35 | 32 | 32 | Other - please specify in text field | Other - please specify in text field-DAMAGE IS BELLOW | Other - please specify in text field | Replace | 09.04.2019 08:03:24 UTC Raju Sutham (QRRSU3) Clear description of the problem. ETP SDU- A CENTRATE LIQUIR BELLOW IS TOTALLY DAMAGED. NEW BELOW TO BE FIXED. PEFS: T-4.253.274 Prioriteit: Additional mitigations : X LOTO/Spading X Block and bleed Electrical tasks: X E-isolation Requester Name : GUPTA Phone : 44032215 20.06.2019 13:12:57 UTC Raj Mohansingh (QRRMOA) BELLOW RMOVED, NEW BWLLOW FIXED [NOTE-bellow is new but from old stock and damaged condition, so as per Mr. Made instruction bellow repaired by PGCC and we fixed and confirmed with OMC and abc ENGR]-job completed
90539188 | 2019-04-25 | A081-0S0163B | 0S-0163B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10294590 | 700002200043 | DKME | Integrity | 0 | 27 | 46 |  |  |  |  | 10.04.2019 00:02:00 UTC Sivakumar Manokaran (QRSMAA) 0S-0163B FILTER DP HIGH NEED TOR EPALCE THE FILTER ELEMENT.
90540121 | 2019-04-21 | A081-294XA-50200-S | 2ET LPU 031;EHT FAULT ALM;BOTH FAULT | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10294801 | 700002607282 |  | Instrumentation | 566.26 | 62 | 140 | Current/voltage -out of limit | Current/voltage -out of limit- | Heat Tracing | Field repair | 12.04.2019 18:21:37 UTC Gopinath Kokoori Vadakkethil (QRGVA2) Clear description of the problem. 294XA 50200: Elec tracng cmn fail alarm on 4 B1 Panel, Changed to RED and vice versa, ET LPU 031; 1SW7401321 RV platform to down step 'U' priority alarm; 4B1 panel PEFS: E.WI.I.CF.00216 Prioriteit: Additional mitigations : Electrical tasks: Requester Name : Gopinath Phone : 44032413
90540162 | 2019-04-23 | A081-0X0104 | 0X-0104 SCREW CONVEYOR CLEANING REQUIRED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10294912 | 700002206193 |  | Electrical | 0 | 6 | 12 | Fouling | Fouling-Conveyour proactive cleaning | Other - please specify in text fields | Cleaned | 14.04.2019 09:40:33 UTC Sivakumar Manokaran (QRSMAA) 0X-0104 screw conveyer cleaning required after DRM batch prepared.
90540778 | 2019-05-04 | A081-2A8324 | DAF 2 SCRAPPER WHELL DAMAGE | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10295462 | 700002297890 | ABB | Electrical | 772.78 | 66 | 66 | Mechanical damage | Mechanical damage- | Other - please specify in text field | Replace | 21.04.2019 01:45:51 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. DAF 2 SCRAPPER SMALL WHEEL PEELED OFF,PROBABLITY IS HIGH TO DAMAGE THE PATHWAY OF THE WHEEL.TO BE FIXED. PEFS: Prioriteit: Additional mitigations : Requester Name : RAJA RAMASAMY Phone : 44032215
90541357 | 2019-04-29 | A081-1A8324 | TR1 DAF SCRAPPER SMALL WHEEL BEARING F01 | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10295841 | 700002348718 |  | Integrity | 71.07 | 86 | 86 | Normal Wear | Normal Wear- | Other - please specify in text field | Replace | 25.04.2019 00:33:19 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. Train 1 DAF scrapper small wheel bearing damage, PEFS: T-4.118.864 Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : Bagus Phone : 44032215
90542344 | 2019-05-21 | A081-2SB200N2 | BA 2R-3121~3123 Top Floor Poor lighting | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10296591 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 4 | 4 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 04.05.2019 07:49:32 UTC Chon Sung Ong (QRCON0) Clear description of the problem. 2R-3121~3123 Reactor top poor Lighting. PEFS: Prioriteit: Additional mitigations : Requester Name : Ong Chon Sung Phone :
90542345 | 2019-05-21 | A081-2SB200N2 | BA LES & CD area G/Floor Poor lighting | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10296592 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 4 | 4 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 04.05.2019 07:51:44 UTC Chon Sung Ong (QRCON0) Clear description of the problem. BA LES <(>&<)> CD area G/Floor Poor lighting PEFS: Prioriteit: Additional mitigations : Requester Name : Ong Chon Sung Phone :
90542346 | 2019-05-15 | A081-294XA-50200-S | 2ET-LPU-91/92/95/97/98 EHT CMN FULT ALM* | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10296613 | 700002607282 |  | Instrumentation | 0 | 8 | 8.5 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault- | Heat Tracing | Other - please specify in text field | 04.05.2019 13:42:20 UTC Manik Kalita (QRMKA4) Phone 33695751 Clear description of the problem. 2SB400E11 CIRCUIT NO 2ET-LPU-91/92/95/97/98 NEED TO BE RESET PEFS: Prioriteit: Electrical tasks: X JHA needed Requester Name : MANIK KALITA Phone : 44032413 05.05.2019 04:45:02 UTC Vijay Paramasivam (QRVPA3) Phone 44032637 ON BACK UP
90543042 | 2019-05-26 | A081-294XA-50200-S | 2ET-LPU-014 EHT FAULT ALM;TAKEN BACKUP | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | LPU | 10297119 | 700002607282 |  | Instrumentation | 4255.06 | 72 | 151 | Current/voltage -out of limit | Current/voltage -out of limit- | Heat Tracing | Field repair | 09.05.2019 21:18:54 UTC Vilas Arande (QRVAR0) Clear description of the problem. 2ET-LPU-014 EHT Fault Alarm on 'MAN' switch changed to 'REDN' then alarm disappeared. PEFS: Prioriteit: Additional mitigations : X JHA needed Requester Name : Vilas Arande Phone : 66478309
90543478 | 2019-06-23 | A081-FIRE HYDRANT | SCE FH229 2.5" VALVE IS PASSING | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10297515 |  |  |  | 433.4 | 6 | 16 | Normal Wear | Normal Wear- | Valve body | Replace | 15.05.2019 06:58:58 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in May 2019, it was found that the 1st (from left to right) 2.5" hydrant delivery valve at fire-hydrant FH229 is passing a continuous stream of water (see marked up attachment). FH229 is located in FGP Phase 2 Area KC, 7th Avenue, opposite 2SS-100. Find attached location and specification details. This water passing from the valve has caused vegetation to grow in front of the hydrant. FM has been notified to remove the vegetation. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684
90544023 | 2019-07-20 | A081-FIRE HYDRANT | SCE FH616 winged cam missing FLARE AREA | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10297518 |  |  |  | 234.39 | 2 | 2 | Normal Wear | Normal Wear- | Other - please specify in text field | Replace | 15.05.2019 07:16:57 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in May 2019, it was found that the Winged Cam Assembly Kit at hydrant FH616 was missing (see marked up attachment). FH616 is located in Flare Area, Opposite Flare Drum 1V-8121. The spare part MM number is 10687723 Find attached location and specification details. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 21.07.2019 01:17:44 UTC Raj Mohansingh (QRRMOA) Winged Cam Assembly(lock)replaced with new one, job completed
90544050 | 2019-06-09 | A081-FIRE HYDRANT | SCE FH608 6" VALVE HANDLE IS BROKEN OFF | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10297517 |  |  |  | 5188.08 | 8 | 19 | Other - please specify in text field | Other - please specify in text field-May be more force during valve operation | Other - please specify in text field | Replace | 15.05.2019 07:08:37 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in May 2019, it was found that the 6" Wafer Lugged Butterfly Valve handle at hydrant FH608 was broken off/faulty (see marked up attachment). FH608 is located in SRU Area, 6th Avenue, opposite Sub-station OSS 600. The spare part MM number is 10687722 Find attached location and specification details. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 21.05.2019 09:51:40 UTC Justin Joseph Kachappilly (QRJKA1) ICC required
90544379 | 2019-06-06 | A081-294XA-50200-S | 2SB 400-E-11 ,EHT COMN FAULT ALARM CHK | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10298177 | 700002607282 |  | Instrumentation | 0 | 12 | 12 | Current/voltage -out of limit | Current/voltage -out of limit-circuit tripped with EL | Heat Tracing | Disconnect / Reconnect | 22.05.2019 21:59:30 UTC Gopinath Kokoori Vadakkethil (QRGVA2) 294XA 50200 ELEC TRACING COMMON FAIL ALARM ON 4 B1 PANEL, TAG 2SB 400-E-11 CAUSE THE ALARM; NEED TO RESET
90544385 | 2019-10-20 | A081-2SB200N2 | BA_LES AND CD AREA_36W LAMPS FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10298374 | 700002373557 | ABB MALAYSIA | Electrical | 2836.93 | 58 | 49 | end of life | end of life- | Lamps |  | 25.05.2019 14:52:54 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER OPS WO# 90542345, BA_LES AND CD AREA 36W/ 18W LAMPS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. 36W TUBE LIGHT- 60 PCs AND 18W TUBE LIGHT- 30 PCs REQUIRED. PEFS: - Prioriteit: X- Step ladder usage Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : MORIA PHONE : 44032804 25.05.2019 15:00:59 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 2SB200N2-02 AND 2SB200N2-04 CIRCUITS 28.07.2019 04:13:38 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804
90545330 | 2019-07-09 | A081-294XA-50200-S | HEAT TRACING ALARM RECTIFY-2SB400E5-Q11 | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10300009 | 700002607282 |  | Instrumentation | 0 | 4 | 20 | Loss of Heating | Loss of Heating- | Other - please specify in text field | Other - please specify in text field | 03.06.2019 07:54:47 UTC Sivaramakrishnan Krishnapandi (QRSKR4) During circuit energize ,MCB tripped due to short circuit of L2 phase. need to be rectify the fault,below tags are connected on this circuit 241QI 10190/TX3-4 and 241QZA 10090/TX2 11.07.2019 12:27:47 UTC Premkumar Dayalan (QRPDA2) Phone 70480663 DISCOVERY SCOPE FOUND - 10306944 NOTIFICATION RAISED.
90545331 | 2019-07-23 | A081-294XA-50200-S | HEAT TRACING ALARM RECTIFY-2SB400E11-Q7 | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10300008 | 700002607282 |  | Instrumentation | 716.04 | 92 | 88 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault-earth fault | Heat Tracing | Disconnect / Reconnect | 03.06.2019 07:47:21 UTC Sivaramakrishnan Krishnapandi (QRSKR4) Heat tracing circuit MCB has tripped frequently,Need to be check and rectify Due to frequent alarm 2SB400E11-Q7 (2ET-LPU-91,92,95,97,98)
90545675 | 2019-06-09 | A081-0S8361A | SDU CENT A ABORTING ON BOWL SPEED ALARM | MX04 | E_MOT_LV | Emergency | 0 |  | CENTRIFUGE | CM | ETP | 10300270 | 700001730109 | ABB | Electrical | 141.85 | 50 | 50 | Power / other utility failure | Power / other utility failure-Bowl Speed probe faulty in field | Instrumentation | Replace | 07.06.2019 06:57:56 UTC Leo Miranda (QRLMI0) Clear description of the problem. SDU CENTRIFUGE A IS ABORTING ON BOWL SPEED ON ALARM. IT IS OBSERVED DURING DECLOGGING THAT BOWL SPEED 083SI60001 (ABS BOWL SPEED) IS NOT MATCHING WITH 083SI60701 (CENTRIFUGE TX SPEED). PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. UNABLE TO PROCESS THE SLUDGE FROM BIOTREATER. What actions did you already take to solve the problem, share information. SEREVAL DECLOGGING AND SEQUENCE DONE, BUT STILL ABORTING ON BOWL SPEED ALARM Additional mitigations : Electrical tasks: Requester Name : LEO Phone : 44032215
90545794 | 2019-06-10 | A081-1A8324 | TR-1 DAF SMALL WHEEL DAMAGE | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10300362 | 700002348718 |  | Integrity | 985.02 | 18 | 18 | Normal Wear | Normal Wear- | drive system | Replace | 09.06.2019 07:34:41 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. ETP FFU TRAIN 1 DAF FLOATER PACKAGE ONE SMALL WHEEL IS DAMAGED. PEFS: T-4.118.864 Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : GUPTA Phone : 44032215
90546246 | 2019-10-05 | A081-1SB210N2 | PM_FLT_U13400_DIFFUSERS DAMAGED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10302383 | 700002352082 | ABB MALAYSIA | Electrical | 1260.48 | 16 | 12 | end of life | end of life- | Casing / enclosure | Replace | 12.06.2019 04:32:40 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER PM WO# 90532900_U13400- FOLLOWING DIFFUSERS FOUND DAMAGED NEED TO BE REPLACED. 1LFN210N2-20L221 - 36W DIFFUSER DAMAGED 1LFN210N2-20L206 - 18W DIFFUSER DAMAGED 1LFN210N2-20L119 - 18W DIFFUSER DAMAGED 1LFN210N2-13L213 - 36W DIFFUSER DAMAGED 1LFN210N2-13L312 - 36W DIFFUSER DAMAGED PEFS: T-4.013.440; T-4.013.449 Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : SANISH PAUL PHONE : 44032804 09.07.2019 12:29:04 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804
90546249 | 2019-09-14 | A081-1SB210N2 | PM_FLT_U13400_1FLN210N2-13L312 DAMAGED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10302385 | 700002352082 | ABB MALAYSIA | Electrical | 571.05 | 10 | 16 | end of life | end of life- | Lighting Fixture | Replace | 12.06.2019 04:38:32 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER PM WO# 90532900_U13400- 1FLN210N2-13L312 36W LIGHT FITTING INTERNAL DAMAGED, NEED TO BE REPLACED. PEFS: T-4.013.449 Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : SANISH PAUL PHONE : 44032804
90546407 | 2019-09-14 | A081-1SB210N2 | PM_FLT_U13400_1FLN210N2-13L112 DAMAGED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10302388 | 700002352082 | ABB MALAYSIA | Electrical | 571.05 | 10 | 16 | end of life | end of life- | Lighting Fixture | Replace | 12.06.2019 04:38:56 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER PM WO# 90532900_U13400- 1FLN210N2-13L112 36W LIGHT FITTING INTERNAL DAMAGED, NEED TO BE REPLACED. PEFS: T-4.013.449 Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : SANISH PAUL PHONE : 44032804
90546647 | 2019-07-06 | A081-1S0241 | 1S-0241 FILTER TO BE CLEANED | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10302775 | 700002354895 | JFC CORPORATION | Integrity | 1804.83 | 24 | 66 |  |  |  |  | 17.06.2019 11:55:19 UTC Sudesh Shetye (QRSSH7) 1S-0241 DP increased to 2.8barg,elememts need to be changed. 18.06.2019 04:45:54 UTC Bakthavatchalan Thenral (QRBTH0) ICC REQUIRED
90546910 | 2019-07-25 | A081-2A8324 | TR2 FFU SCRPER REAR WHEEL DAMAGED FO1 | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10302759 | 700002297332 |  | Integrity | 123.59 | 0 | 93 | Other - please specify in text field | Other - please specify in text field-damage wheel | Other - please specify in text field | Replace | 17.06.2019 10:10:28 UTC Eric Ates (QREAT0) Clear description of the problem. TR2 DAF SCRAPPER REAR SMALL WHEEL ROAD SIDE OBSERVED DAMAGED CONDITIONED.WHEEL NEEDS TO BE REPLACED. PEFS: T-4.118.867 Prioriteit: Additional mitigations : X Scaffold Requester Name : ERIC ATES Phone : 44032215 28.07.2019 21:49:33 UTC Arunbhai Patel (QRAPA0) Replaced new 2 no scrper rear wheel
90547002 | 2019-07-10 | A081-294XA-50200-S | 294XA-50200-S1 COMMON FAULT ALM;REW2** | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10302972 | 700002607282 |  | Instrumentation | 256.68 | 45.5 | 34.5 | Current/voltage -out of limit | Current/voltage -out of limit- | Heat Tracing | Field repair | 20.06.2019 06:10:12 UTC Gopinath Kokoori Vadakkethil (QRGVA2) U priority electric tracing common fail alarm in 4 B1 Panel, Not related to any particular tag; common alarm;
90547012 | 2019-06-24 | A081-0S0163B | OS0163B FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10303203 | 700002200043 | DKME | Integrity | 357.43 | 27 | 46 |  |  |  |  | 22.06.2019 23:49:17 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. OS0163B FILTER EXHAUSTED AND FILTER ELEMENT TO BE REPLACE PEFS: Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. 0S-0163 A TKEN IN SERVICE Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115 23.06.2019 07:14:58 UTC Bakthavatchalan Thenral (QRBTH0) ICC Required
90547311 | 2019-06-25 | A081-0S8361A | 0SM8361A2 NOT STARTING | MX04 | E_MOT_LV | Emergency | 0 |  | CENTRIFUGE | CM | ETP | 10303652 | 700001730110 | ABB | Electrical | 0 | 35 | 0 | Human Error | Human Error-Durng reset,incidentaly pres R/L buttton | Control Circuit | Adjust / reset | 25.06.2019 23:33:12 UTC Leo Miranda (QRLMI0) 0SM--8361A2 not getting started need to check PEFS: Prioriteit: Additional mitigations : X JHA needed quester Name DAVID Phone:44032215
90547360 | 2019-06-26 | A081-1A8324 | DAF1 SCRAPER SCUM TROUGH DAMAGED | MX04 | M_X_X | Emergency | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10303671 | 700002348718 |  | Integrity | 6652.19 | 200 | 0 | Other - please specify in text field | Other - please specify in text field-scum trough | Other - please specify in text field | Fix / Repair | 26.06.2019 02:13:42 UTC Leo Miranda (QRLMI0) Clear description of the problem. TRAIN 1 DAF SCRAPER SCUM TROUGH IS IN LIFTED POSITION UNABLE TO RUN THE SCRAPER PASS THROUGH IT DUE TO POTENTIAL ENTANGLING, ONE SCUM BOARD FOUND DAMAGED CONDITION PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. NO SCUM REMOVAL, HIGH COD LOADING TO BIOTREATER. What actions did you already take to solve the problem, share information. SLUDGE WASTING STOPPED, CHEMICAL DOSING STOPPED, AND PROCESSING FLOW REDUCED. Additional mitigations : Electrical tasks: X E-isolation Requester Name : LEO Phone : 44032215 26.06.2019 06:58:59 UTC "Lourdhu Ponnusamy, " Thomas (QRTPO0) Scaffolding ,HVAC,REST SHELTER REQUIRED FOR PREPARATION -THOMAS
90547618 | 2019-07-20 | A081-2SB200N2 | BA area GF Auto light Sensor malfunction | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10304223 | 700002373557 | ABB MALAYSIA | Electrical | 811.29 | 8 | 33 | end of life | end of life- | Electronic / control board | Replace | 29.06.2019 10:53:48 UTC Chon Sung Ong (QRCON0) Clear description of the problem. auto Light up lighting in BA Area (2SB200N2-OR-SW1) Ground Level Plant lighting. (normally Off) means Light will AUTO ON But if we put Switch OFF position(Normal) Lighting not light up during night. Means auto Light sensor not function. Now Light switch in Override (ON position)During Night Shift. PEFS: Prioriteit: Additional mitigations : Requester Name : Ong Chon Sung Phone : HPS Tr-2
90548086 | 2019-07-03 | A081-1SB210N2 | EX 36W FIXTURE DIFFUSER DAMAGED | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10304661 | 700002352082 | ABB MALAYSIA | Electrical | 73.8 | 6 | 0 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace | 01.07.2019 09:25:09 UTC Mageshkumar Rajaram (QRMRA1) Phone 44032804 2804 Clear description of the problem. During our walk down, observed 36W Tube lamp fixture diffuser damaged (Big hole), need to replaced asap. This fixtures losses EX integrity 1) 1LFN210N220L119 2) 1LFN220N212L216 PEFS: Prioriteit: X JHA needed Requester Name : MAGESHKUMAR RAJARAM Phone : 31548616 03.07.2019 11:45:04 UTC Sudheer Kumar Pendurthi (QRSPE6) WE ARE REPLACED ONLY 1LFN210N220L119 THIS FIXTURE.ANOTHER ONE (1LFN220N212L216) WE WILL DO ON THIS PERMIT: A081-00-0685128
90548636 | 2019-09-15 | A081-0S0143A | 0S-0143A DP HIGH FILTER ELEMENT TO BE RE | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10305835 | 700002201324 | DKME | Integrity | 3737.23 | 27 | 46 |  |  |  |  | 05.07.2019 18:38:11 UTC Sivakumar Manokaran (QRSMAA) 0S-0143A filter DP high filter element to be repalced. 07.07.2019 04:45:26 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90548676 | 2019-09-12 | A081-1SB210N2 | PM_FLT_U13000_18W/ 36W LIGHT FITTINGS | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10305384 | 700002352082 | ABB MALAYSIA | Electrical | 36.9 | 10 | 6 | Operating at high temperature | Operating at high temperature- | Lighting Fixture | No action | 03.07.2019 14:25:11 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER SCE Ex PM WO# 90531763_U13000- ALL 18W/ 36W LIGHT FITTINGS TOP OF FINFAN PLATFORM; RV AREA GETTING OVERHEATED, OUTSIDE FULLY ERODED AND CHANCE OF BREAKDOWN, ERE- ANALYSIS TO BE DONE/ ALL NEED TO BE REPLACED. Ex INTEGRITY RELATED SYMPTOMS. PEFS: - Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : MORIA PHONE : 44032804 04.07.2019 04:54:35 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 ATTACHED COPY OF QAQC FORM FOR REFERENCE 30.07.2019 07:21:17 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804
90548677 | 2019-11-09 | A081-1SB210N2 | PM_FLT_U13000_18W/ 36W DIFFUSERS DAMAGED | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10305383 | 700002352082 | ABB MALAYSIA | Electrical | 15595.77 | 78 | 66 | end of life | end of life- | Casing / enclosure | Replace | 03.07.2019 14:02:03 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER SCE Ex PM WO# 90531763_U13000- FOLLOWING LIGHT FITTING DIFFUSERS FOUND DAMAGED CONDITION, NEED TO BE REPLACED. Ex INTEGRITY RELATED SYMPTOMS. 36W DIFFUSER DAMAGED- 60 PCs 18W DIFFUSER DAMAGED- 10 PCs PEFS: - Prioriteit: Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : MORIA PHONE : 44032804 04.07.2019 04:58:48 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804
90548798 | 2019-10-27 | A081-1SB220N2 | 1LFN220N2-25L107 36W FITTING INT-DAMGAED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10305982 | 700002356603 | ABB MALAYSIA | Electrical | 553.12 | 10 | 45 | Operating at high temperature | Operating at high temperature- | Lighting Fixture | Replace | 07.07.2019 08:57:32 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. DURING CM ACTIVITY AT AC AREA, NEAR 1R-1112, FOUND 36W TUBELIGHT FITTING INTERNAL DAMAGED, NEED TO BE REPLACED WITH NEW. PEFS: T-4.013.359 Priority: X- Scaffolding required Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : VEERRAJU PHONE : 44032804 08.07.2019 11:49:10 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Ex/ IP INTEGRITY IS OK, ONE FITTING ONLY FAULTY CAN BE ATTENDED AS PER PLANNING/ SCHEDULING. 26.08.2019 09:04:11 UTC Manoj Singh (QRMSI7) located at hot area, as per DPM WOW asigned
90549076 | 2019-10-22 | A081-1SB220N2 | 1LFN220N2-18L106 36W FITTING INT-DAMGAED | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10305983 | 700002356603 | ABB MALAYSIA | Electrical | 133.89 | 10 | 50 | Operating at high temperature | Operating at high temperature- | Lighting Fixture | Replace | 07.07.2019 08:58:21 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. DURING CM ACTIVITY AT AC AREA, NEAR 1R-1112, FOUND 36W TUBELIGHT FITTING INTERNAL DAMAGED, NEED TO BE REPLACED WITH NEW. PEFS: T-4.013.360 Priority: X- Scaffolding required Electrical tasks: X E- Personal isolation X JHA needed Requester NAME : VEERRAJU PHONE : 44032804 08.07.2019 11:51:30 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Ex/ IP INTEGRITY IS OK, NO ISSUE AS INTERNAL DAMAGE ONLY. ONE FITTING ONLY FAULTY CAN BE ATTENDED AS PER PLANNING/ SCHEDULING.
90549090 | 2019-07-11 | A081-1S0241 | 1S-0241 DP IS INCREASING TREND | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10306381 | 700002354895 | JFC CORPORATION | Integrity | 1727.94 | 22 | 65 |  |  |  |  | 09.07.2019 09:03:33 UTC Farooq Ahmad (QRFAH0) Clear description of the problem. 1S-0241 DP is in increasing trend, need to be prioritize to replace in near future, as TR-1 load is high (This SAP is raised as per PS instruction- in advance) PEFS: T-13.370.089 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Yes because 1S-0241 amine filtration is not 100% effective and TR-1 DP issue is frequently occuring. What actions did you already take to solve the problem, share information. Raised notification Additional mitigations : Requester Name : Pratik Prajapati
90549152 | 2019-10-21 | A081-2SB200N2 | 2SS200 HVAC room lights not working | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10306725 | 700002373557 | ABB MALAYSIA | Electrical | 522.25 | 6 | 100 | end of life | end of life- | Lamps | Replace | 10.07.2019 11:35:05 UTC RAJKUMAR KUPPUSAMY (QRRKUG) Clear description of the problem. 2SS200, HVAC Room lights are not working, please rectify. PEFS: Prioriteit: Additional mitigations : Requester Name : Abdul Shabeer Phone : 70241543
90549481 | 2019-12-04 | A081-294XA-50200-S | 241QI10190/TX-4 EHT ALARM FAULT;COMN ALM | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10306944 | 700002607282 |  | Instrumentation | 188.53 | 16 | 22 | Open loop / short circuit / earth fault | Open loop / short circuit / earth fault- | Heat Tracing | Field repair | 11.07.2019 12:24:14 UTC Premkumar Dayalan (QRPDA2) Phone 70480663 Clear description of the problem. IN CONNECTION WITH W/O - 90545330 NOTIF-10300009, FIND 241QI-10190/TX-4 CIRCUIT, HEAT TRACING ELEMENT FAULTY. NEED TO REPLACE PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : PREMKUMAR Phone : 70483989 04.12.2019 12:46:08 UTC Premkumar Dayalan (QRPDA2) Phone 70483989 Found end terminal was short circuited. Checked and Fault portion cut off and end cap provided. Now working normal
90549780 | 2019-07-15 | A081-0S0163A | 0S-0163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10307771 | 700002200042 | DKME | Integrity | 448.89 | 27 | 46 |  |  |  |  | 16.07.2019 01:23:45 UTC Elangovan Muthusamy (QREMU0) 0S-0163A DP high filter to be replaced.
90549904 | 2019-07-16 | A081-1S0241 | 1S-0241 DP INCREASING TREND | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10307821 | 700002354895 | JFC CORPORATION | Integrity | 1761.19 | 22 | 61 |  |  |  |  | 16.07.2019 06:19:54 UTC Antony Elvin Wilson (QRAWI1) Clear description of the problem. 1S-0241 DP is in increasing trend, need to be prioritize to replace in near future, as TR-1 load is high (This SAP is raised as per PS instruction- in advance) PEFS: T-13.370.089 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Yes because 1S-0241 amine filtration is not 100% effective and TR-1 DP issue is frequently occuring. What actions did you already take to solve the problem, share information. Raised notification Additional mitigations : Requester
90550292 | 2019-10-05 | A081-2SB210N2 | BB AREA LIGHT FITITING DIFFUSERS DAMAGED | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10309086 | 700002373562 | ABB MALAYSIA | Electrical | 5106.67 | 18 | 16.1 | Mechanical damage | Mechanical damage- | Lighting Fixture |  | 20.07.2019 22:49:44 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. AS PER PM WO# 90532907, VISUAL INSPECTION MADE AND REFER FOR OBSERVATION IN ATTACHED QAQC, EX INTEGRITY RELATED SYMPTOMS. 1) 18W DIFFUSER FAILED- 2 PCs TO BE REPLACED 2) 36W DIFFUSER FAILED- 19 PCs TO BE REPLACED (FOR ACCESS WE WILL DO BY 'A' TYPE LADDER) PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : MORIA SINH PRATAP Phone : 4403 2804
90550455 | 2019-10-17 | A081-1SB220N2 | AC_AREA LIGHT FITITING DIFFUSERS DAMAGED | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10309304 | 700002356603 | ABB MALAYSIA | Electrical | 2576.77 | 18 | 16 | end of life | end of life- | Casing / enclosure | Replace | 22.07.2019 00:16:29 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. AS PER PM WO# 90532902, VISUAL INSPECTION MADE AND REFER FOR OBSERVATION IN ATTACHED QAQC, EX INTEGRITY RELATED SYMPTOMS. 1) 36W DIFFUSER FAILED- 10 PCs TO BE REPLACED 2) 1LFN220N224L104 36w FIXTURE HANGING CONDITION NOTE; WE CAN DO BY 'A' TYPE LADDER PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : SHYAM TIWARI Phone : 4403 2804
90550467 | 2019-07-21 | A081-1S0241 | 1S-0241 FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10309305 | 700002354895 | JFC CORPORATION | Integrity | 1727.94 | 22 | 61 |  |  |  |  | 22.07.2019 00:50:07 UTC Murahari Korlam (QRMKO0) 1S-0241 DP is in increasing trend. Filter element to be replaced.
90550495 | 2019-08-05 | A081-0S0163A | 0S-0163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10309220 | 700002200042 | DKME | Integrity | 1795.96 | 27 | 46 |  |  |  |  | 21.07.2019 11:16:52 UTC Elangovan Muthusamy (QREMU0) 0S-0163A DP high filter element to be replaced.
90550496 | 2019-11-30 | A081-0S0163A | 0S-0163A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10309219 | 700002200042 | DKME | Integrity | 3808.17 | 27 | 46 |  |  |  |  | 21.07.2019 11:15:49 UTC Elangovan Muthusamy (QREMU0) 0S-0163A DP high filter element to be replaced.
90550497 | 2019-07-29 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10309221 | 700002200043 | DKME | Integrity | 551.64 | 27 | 46 |  |  |  |  | 21.07.2019 11:18:31 UTC Elangovan Muthusamy (QREMU0) 0S-0163B DP high filter element to be replaced.
90550498 | 2019-09-29 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10309223 | 700002200043 | DKME | Integrity | 3929.32 | 27 | 46 |  |  |  |  | 21.07.2019 11:20:59 UTC Elangovan Muthusamy (QREMU0) 0S-0163B DP high filter element to be replaced.
90550499 | 2019-12-25 | A081-0S0143A | 0S-0143A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10309226 | 700002201324 | DKME | Integrity | 1648.72 | 27 | 46 |  |  |  |  | 21.07.2019 11:24:41 UTC Elangovan Muthusamy (QREMU0) 0S-0143A DP high filter element to be replaced.
90550500 | 2019-12-02 | A081-0S0143A | 0S-0143A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10309224 | 700002201324 | DKME | Integrity | 1477.27 | 27 | 46 |  |  |  |  | 21.07.2019 11:22:58 UTC Elangovan Muthusamy (QREMU0) 0S-0143A DP high filter element to be replaced.
90550501 | 2019-07-31 | A081-0S0143B | 0S-0143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10309227 | 700002202402 | DKME | Integrity | 357.35 | 27 | 46 |  |  |  |  | 21.07.2019 11:27:20 UTC Elangovan Muthusamy (QREMU0) 0S-0143B DP high filter element to be replaced.
90550502 | 2020-01-01 | A081-0S0143B | 0S-0143B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10309228 | 700002202402 | DKME | Integrity | 1791.57 | 27 | 46 |  |  |  |  | 21.07.2019 11:28:57 UTC Elangovan Muthusamy (QREMU0) 0S-0143B DP high filter element to be replaced.
90551064 | 2019-07-27 | A081-1S0241 | 1S-241 FILTER REPLACEMENT WITH 5 MICRON | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10310570 | 700002354895 | JFC CORPORATION | Integrity | 2328.4 | 22 | 61 |  |  |  |  | 26.07.2019 06:42:45 UTC Justin Joseph Kachappilly (QRJKA1) 1S-241 element replacement with 5 micron
90551172 | 2019-08-05 | A081-2SB210N2 | FS-2E3024~26 Exch All Flr Light not work | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10310477 | 700002373562 | ABB MALAYSIA | Electrical | 110.71 | 10 | 2 | Internal failure / short | Internal failure / short-2LFN210N226L205 FITTING WAS FAULTY | Lamps | Check/ Inspect/ Test | 25.07.2019 22:33:32 UTC Chon Sung Ong (QRCON0) Clear description of the problem. BB Area, 2E3024~2E3026 Exchanger side all floor Light not Working. PEFS: Prioriteit: Additional mitigations : Requester Name : Ong Chon Sung Phone : 06.08.2019 01:41:46 UTC Sudheer Kumar Pendurthi (QRSPE6) FOUND 2LFN210N226L205 FITTING WAS FAULTY AND RAISED NOTIFICATION ; 10312891.NORMALIZED REMAINING CIRCUITS, NOW OK
90551261 | 2019-08-06 | A081-2SB200N2 | 2R3121 Top reactor Flood light not work | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10310669 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 2 | 9.1 |  |  |  |  | 27.07.2019 22:25:23 UTC Chon Sung Ong (QRCON0) Clear description of the problem. Train 2 BA area, 2R-3121 top floor Flood light not working PEFS: Prioriteit: Additional mitigations : Requester Name : Ong Phone : 29.07.2019 08:48:41 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 SINCE NOTIFICATION CREATED BY OPS AND NO CLEAR INFORMATION ABOUT NUMBER AND FAULTY TAGS LIST, NEED INSPECTION AND NEW NOTIFICATIONS TO BE CREATED. 02.08.2019 07:08:19 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 WAPP WORKORDERS ALREADY AVAILABLE, 90544397, 90544398, 90544396, 90544401, 90544403, 90544395 FOR 2R-3121, 2R-3122, 2R-3123 AREA 02.08.2019 15:07:30 UTC Srinivasa Dandu (QRSDA3) Covered in above WO hence this SAP is cancelled
90551455 | 2019-07-31 | A081-0S8361A | 0M8361A1 command disagree | MX04 | E_MOT_LV | Emergency | 0 |  | CENTRIFUGE | CM | ETP | 10311651 | 700001730109 | ABB | Electrical | 637.77 | 76 | 8 | Misalignment | Misalignment- | Electronic / control board | Adjust / reset | 30.07.2019 11:41:02 UTC Mohanraj Chellaih (QRMCH0) Clear description of the problem. 0M8361A1 having command disagree alarm ,motor not getting started for cleaning Unit got tripping twice in the shift due to bowel motor PEFS: T-44.253.274 Prioriteit: Additional mitigations : Requester Name : Mohan Phone : 44032215 31.07.2019 09:12:11 UTC Lincoln Christopher (QRLCH1) Job completed .
90552024 | 2019-08-04 | A081-1S0241 | 1S-0241 FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10312732 | 700002354895 | JFC CORPORATION | Integrity | 1094.59 | 22 | 61 |  |  |  |  | 03.08.2019 23:36:52 UTC Prashant Tamhane (QRPTA0) 1S-0241 DP is high , need to replace filter element PEFS: T-13.370.089 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. HIgh DP could buckeled the filter. What actions did you already take to solve the problem, share information. Raised notification Additional mitigations : Requester 04.08.2019 07:05:45 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90552052 | 2019-08-18 | A081-0X0104 | 0X-0104 SCREW CONVEYOR CLEANING | MX04 | M_PAC_CON2 | Routine Wrk Lvl 3 | 0 |  | SCREW CONVEYOR | CM | FGP | 10312568 | 700002206193 |  | Electrical | 0 | 6 | 12 | Fouling | Fouling- | drive system | Cleaned | 01.08.2019 08:46:04 UTC Elangovan Muthusamy (QREMU0) 0X-0104 screw conveyor to be cleaned for next batch preparation. 04.08.2019 09:37:46 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90552190 | 2019-08-06 | A081-0S8361A | SDU A TRIPPING IN BOWL SPEED FO3 | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10312764 | 700001729713 |  | Rotating | 0 | 32 | 32 | Product Contamination | Product Contamination-Product deposit | Other - please specify in text field | Cleaned | 04.08.2019 07:07:13 UTC Eric Ates (QREAT0) Clear description of the problem. SDU A FREQUENTLY TRIPPING IN BOWL SPEED ISSUE.CENTRIFUGE INSPECTION REQUIRED.TOP COVER TO BE REMOVE TO CHECK CENTRIFUGE INTERNAL FOR CLEANING AND OTHER JOBS. PEFS: T-4.258.845 Prioriteit: Additional mitigations : Requester Name : ERIC ATES Phone : 44032215 05.08.2019 15:13:21 UTC "Lourdhu Ponnusamy, " Thomas (QRTPO0) AS PER RE BASKAR,TOP COVER TO BE OPENED AND CLEANED - FOR MORE INFORMATION CALL RE- BASKAR. 07.08.2019 01:53:41 UTC Kolappan Ramalingom Asari (QRKRA0) Centrifuge internal cleaning done, job completed, sap closed.
90552759 | 2019-08-24 | A081-294XA-50200-S | 294XA 50200 ELEC TRCNG CMN FAIL ALARM | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10313017 | 700002607282 |  | Instrumentation | 0 | 10 | 10 | Leakage | Leakage-earth fault (2SB400E11-Q15) | Fuse / MCB | Repair / correct | 07.08.2019 07:48:09 UTC Gopinath Kokoori Vadakkethil (QRGVA2) ELEC TRCNG CMN FAIL ALARM ON 4 B1 PANEL - 'U'PRIORITY 2SS 400 E11_Q15 SWITCH GIVING THE ALARM; NEED TO REPAIR
90552760 | 2019-08-12 | A081-2SB200N2 | HSSE-BAAREA LIGHT FTING DIFFUSERSDAMAGED | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10313298 | 700002373557 | ABB MALAYSIA | Electrical | 101.45 | 8 | 8 | Mechanical damage | Mechanical damage- | Lighting Fixture |  | 11.08.2019 01:19:46 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. AS PER PM WO# 90532909, VISUAL INSPECTION MADE OBSERVATION EX INTEGRITY RELATED SYMPTOMS. 1) 36W DIFFUSER DAMAGED- 02 PCs TO BE REPLACED (2LLFN200N215L206, 2LLFN200N212L206) 2) 18W DIFFUSER DAMAGED- 02 PCs TO BE REPLACED (2LLFN200N219L105, 2LLFN200N219L206) NOTE; WE CAN DO BY 'A' TYPE LADDER PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : MORIA PRATAPSINH Phone : 4403 2804
90552763 | 2019-08-11 | A081-1S0241 | 1S-0241 FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10313285 | 700002354895 | JFC CORPORATION | Integrity | 0 | 22 | 61 |  |  |  |  | 10.08.2019 19:10:33 UTC Pratik Manilal Prajapati (QRPPR1) 1S-0241 DP is in increasing trend need to replace filter element. PEFS: T-13.370.089 Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. HIgh DP could buckeled the filter. What actions did you already take to solve the problem, share information. Current DP is 1.4 barg. Proactively raised notification as we have to isolate the filter once DP reach 1.8barg Additional mitigations : 11.08.2019 07:44:44 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90553032 | 2019-08-15 | A081-1SB220N2 | HSSE-AD_AREA LIGHT FITITING DIFF DAMAG | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10313391 | 700002356603 | ABB MALAYSIA | Electrical | 161.95 | 8 | 37 | Mechanical damage | Mechanical damage- | Lighting Fixture |  | 12.08.2019 11:37:23 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER PM WO_90532904, REPORTED AD PIPE RACK AREA, FOLLOWING LIGHT FITTINGS DIFFUSERS FOUND DAMAMGED CONDITION, NEED TO BE REPLACED WITH LAMPS/ DIFFUSERS. 1LFN220N2-09L212 36W FITTING - S/F REQD 1LFN220N2-09L304 18W FITTING - LADDER 1LFN220N2-24L131 36W FITTING - LADDER 1LFN220N2-24L211 36W FITTING - LADDER 1LFN220N2-24L316 36W FITTING - LADDER 1LFN220N2-24L212 36W FITTING - LADDER 1LFN220E1-04L314 36W FITTING - LADDER PEFS: - Prioriteit: Clear description of the problem, answer the following questions : Electrical tasks: X E-isolation X JHA needed
90553037 | 2019-09-14 | A081-1SB220N2 | PM_FLT_AD_1LFN220N2-24L303 36W FITT DAMA | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10313392 | 700002356603 | ABB MALAYSIA | Electrical | 639.78 | 10 | 50 | end of life | end of life- | Lighting Fixture | Replace | 12.08.2019 12:06:57 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 Clear description of the problem. AS PER PM WO_90532904, REPORTED AD PIPE RACK AREA, 1LFN220N2-24L303 36W LIGHT FITTING INTERNAL DAMAMGED CONDITION, NEED TO BE REPLACED WITH NEW FITTING. PEFS: T-4.013.411 Prioriteit: X Scaffold required Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : VEERRAJU Phone : 4403 2804
90553300 | 2019-09-16 | A081-1A8324 | TR1 DAF SCUM TROUGH REPLACEMENT FO1*CSE | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10313585 | 700002348718 |  | Integrity | 78058.95 | 583 | 2070 | Mechanical damage | Mechanical damage- | Plate-cladding | Replace | 14.08.2019 21:17:15 UTC Eric Ates (QREAT0) Clear description of the problem. DAF1 SCUM TROUGH REPLACEMENT REQUIRED.DAF1 HAS BEEN OPERATING IN CRIPPLED MODE DUE SCUM TROUGH ISSUE WHICH IS AFFECTING DAF PERFORMA NCE.SCAFFOLDING REQUIRED FOR THIS JOB. PEFS: T-4.118.864 Prioriteit: Additional mitigations : X WPS/ Work instruction needed Requester Name : ERIC ATES Phone : 44032215 23.10.2019 10:59:27 UTC Yogarajan Pandiyan (QRYPA0) SCUM BOX REPLACED. NEW SCUM SUPPORT STRUCTURE MODIFIED TO MATCH WITH SITE REQUIREMENTS AS PER TA ADVICE.
90553853 | 2019-01-01 | A081-1S0241 | 1S-0241 FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10313865 | 700002354895 | JFC CORPORATION | Integrity | 947.87 | 22 | 61 |  |  |  |  | 19.08.2019 23:17:48 UTC Rajesh Chandra Sekhara Pillai (QRRPI4) 1S-0241 DP is in increasing trend need to replace filter element. PEFS: T-13.370.089 Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. HIgh DP could buckeled the filter. What actions did you already take to solve the problem, share information. Current DP is 1.5 barg. Proactively raised notification as we have to isolate the filter once DP reach 1.8barg Additional mitigations : 20.08.2019 04:49:19 UTC Bakthavatchalan Thenral (QRBTH0) ICC Required
90554041 | 2020-12-24 | A081-1F5111 | PROCURE SPARE 1/2F5111 BNR ASSEMBLY” | MX09 | M_FUR_X | Routine Wrk LvL 5 | 0 |  | SMR FURNACE | CM | LPU | 10313914 | 700002348459 | KTI | Integrity | 112504.98 | 0 | 0
90554627 | 2019-08-28 | A081-1S0241 | 1S-0241 FILTER ELEMENTS TO BE REPLACED | MX09 |  | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10314245 |  |  |  | 1305.31 | 22 | 61 |  |  |  |  | 26.08.2019 11:05:25 UTC Murahari Korlam (QRMKO0) 1S-0241 DP is in increasing trend need to replace filter element. PEFS: T-13.370.089 Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. HIgh DP could buckeled the filter. What actions did you already take to solve the problem, share information. Current DP is 1.6 barg. Proactively raised notification as we have to isolate the filter once DP reach 1.8barg 27.08.2019 04:37:51 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90554731 | 2020-02-17 | A081-2A8324 | TR2 DAF OUTLET SAMPLE VALVE NOT WORKING | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10314094 | 700002297332 |  | Integrity | 99.73 | 20 | 20 | Other - please specify in text field | Other - please specify in text field-VALVE HANDLE FOUND DAMAGE | Valve body | Replace | 23.08.2019 10:26:10 UTC Joyabrata Gupta (QRJGU0) Clear description of the problem. TRAIN 2 DAF OUTLET TO 2T-8346 LINE SAMPLE COLLECTION POINT VALVE HANDLE DAMAGE. SAMPLE COLLECTION VALVE NEED REPLACEMENT PEFS: T-4.118.867 Prioriteit: Additional mitigations : X Single valve insolation Requester Name : GUPTA Phone : 44032215 27.08.2019 16:09:22 UTC Raju Sutham (QRRSU3) SAMPLE LINE NEEDLE VALVE HANDLE BROKEN CONDITION, NEED TO REPLACE 17.02.2020 14:38:03 UTC Vudumudi Ravikumar (QRRVU1) TRAIN 2 DAF OUTLET TO 2T-8346 LINE SAMPLE COLLECTION POINT VALVE REPLACE WITH NEW VALVE
90554759 | 2019-08-28 | A081-2A8324 | TR-2 DAF SMALL WHEEL LINER DAMAGED | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10314344 | 700002297332 |  | Integrity | 815.92 | 22 | 22 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace | 27.08.2019 19:57:40 UTC Srinivasan Ramasamy (QRSRAE) Clear description of the problem. TR2 DAF SCRAPPER SMALL WHEEL LINER DAMAGED PEELED OFF CONDITION, IT MAY DAMAGE THE RUN WAY, SMALL WHEEL NEED TO BE REPLACED. PEFS: T-4.118.867 Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation Requester Name : SRINIVASAN Phone : 44032215 29.08.2019 01:42:15 UTC Arunbhai Patel (QRAPA0) Replaced new small wheel .
90554905 | 2019-09-11 | A081-2A8324 | TR2 DAF SCRAPER SMALL WHEEL 3 NOS CHANGE | MX04 | E_MOT_LV | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10314475 | 700002297890 | ABB | Electrical | 1376.8 | 8 | 66 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace | 29.08.2019 01:31:59 UTC Leo Miranda (QRLMI0) Clear description of the problem. 3 NOS OF SMALL WHEEL IN DAF SCRAPPER TO BE CHANGED AS SOON AS POSSIABLE BECAUSE SMALL WHELL TOP LAYER RUBBER IS LOOSEN AND METAL PORTION OF THE WHEEL IS VISIBLE . PEFS: Prioriteit: Additional mitigations : Requester Name : RAJA RAMASAMY Phone : 44032215 12.09.2019 01:55:55 UTC Arunbhai Patel (QRAPA0) Removes damage small wheel replaced new 3 nos small wheel.
90555441 | 2019-09-25 | A081-1A8324 | DAF-1 EMPTYOUT SUPPORT FOR HOSE CONNECT | MX09 | M_X_X | Routine Wrk Lvl 4 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10313799 | 700002348718 |  | Integrity | 3994.73 | 160 | 160 | Product Contamination | Product Contamination-DAF EMPTY OUT FOR REPAIRING | Other - please specify in text fields | Cleaned | 18.08.2019 23:40:49 UTC Srinivasan Ramasamy (QRSRAE) Clear description of the problem. TRAIN-1 DAF 1A-8324 EMPTY OUT SUPPORT FOR DIESEL PUMP / HOSE MOBILISATION, CONNECTION AND DISCONNECTION. PEFS: Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. OPS WILL SHOW THE HOSES X Crane CRANE REQUIRED TO PUT THE SUCTION HOSE INSIDE DAF UNIT X JHA needed Requester Name : SRINIVASAN RAMASAMY Phone : 44032215 20.10.2019 08:38:19 UTC Raj Mohansingh (QRRMOA) HOSE SHIFTED NRAR DAF-1 FOR EMPTYOUT, CONNECT AS PER OPS REQUIRMENT, DAF EMPTY OUT, AFTER COMPLETED DAF DISCONNECT THE HOSE, REMOVED AND SHIFTED IN HOSE SHED AREA, HOUSE KEEPING DONE, JOB COMPLETED
90556308 | 2019-09-11 | A081-1S0241 | 1S-0241 filter dp high filter replacemen | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10315338 | 700002354895 | JFC CORPORATION | Integrity | 1192.68 | 22 | 61 |  |  |  |  | 08.09.2019 13:14:05 UTC Edwin Reyes (QRERE0) 1S-0241 DP is in increasing trend need to replace filter element.DP-1.42barg need to clean on 1.8barg as per tech. PEFS: T-13.370.089 Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. HIgh DP could buckeled the filter. What actions did you already take to solve the problem, share information. Current DP is 1.42 barg. Proactively raised notification as we have to isolate the filter once DP reach 1.8barg Additional mitigations : ICC required 09.09.2019 04:58:23 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90556931 | 2020-01-09 | A081-0X0104 | 0X-0104 DR M FILTER CONVEYOR TO BE CLEAN | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10316250 | 700002206193 |  | Electrical | 0 | 6 | 12 | Fouling | Fouling- | rollers | Cleaned | 12.09.2019 15:29:02 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0X-0104 DR M FILTER CONVEYOR TO BE CLEANED AFTER FRESH BATCH PREPARATION. PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. CONVEYOR MOTOR WILL TRIP WHILE FRESH BATCH PREPARATION What actions did you already take to solve the problem, share information. CONVEYOR TO BE CLEANED BEFORE FRESH BATCH PREPARATION Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90556953 | 2019-10-29 | A081-1SB210N2 | 1R3022 top manway permanent light busted | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10316316 | 700002352082 | ABB MALAYSIA | Electrical | 765.49 | 8 | 8 | end of life | end of life- | Lamps | Replace | 13.09.2019 22:25:07 UTC Alvin Englis Siglos (QRASI2) Clear description of the problem. During safety walkdown on 1R-3022 CCO activity, it was noticed that the permanent lighting facility near reactor top manway was not working. The two lights were suspected busted causing a minimal poor lighting condition on the catalyst change out activity. Fixing this lighting will ensure a consistent good working condition at that location. PEFS: NA Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. Inform work party to arrange temporary lighting facility. Additional mitigations : Requester Name : ALVIN SIGLOS Phone : 44032314 29.10.2019 12:12:23 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 EQ ID CHANGED TO A081-1SB210N2
90557040 | 2019-09-17 | A081-1SB210N2 | HSSE:LIGHT FIXTURE & CABLE DAMAGED-AB | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10316387 | 700002352082 | ABB MALAYSIA | Electrical | 142.76 | 10 | 0 | Operating at high temperature | Operating at high temperature- | Lighting Fixture | Repair / correct | 15.09.2019 10:37:00 UTC Mageshkumar Rajaram (QRMRA1) Phone 44032804 2804 Clear description of the problem. LIGHT FIXTURE, DIFFUSER DAMAGED <(>&<)> CABLE ARMOUR EXPOSED AND OUTERSHEATH DAMAGED AT SOME PLACES TOTAL FIXTURES 25APPROX, 5 FIXTURES NEED TO REPLACE IMMEDIATLY REST OFF DIFFUSER TO BE REPLACED LOCATION: 27.200MTRS, ABOVE FIN FAN PLATFORM - AB AREA 4 FIXTURES NEED TO REPLACE ASAP DUE TO EX INTEGRITY FAILED HIGH TEMPERATURE NEED MITIGATION PEFS: T-4.013.443 (1LFE210E102L326, 1LFN210N211L320, 1LFN210N211L121, 1LFN210N212L218) Prioriteit: Electrical tasks: X E-Disconnect X E-isolation Requester Name : MAGESHKUMAR Phone : 31548616 16.09.2019 07:54:33 UTC Sankaran Kutty Marar Muraleedharan (QRSMU4) This WO will use for disconnection of cables as immedate action. New WO will be created for repair job 18.09.2019 12:38:23 UTC Sudheer Kumar Pendurthi (QRSPE6) Bellow mention lighting fixture cable disconnected from JB. 1LFN210N211L320 CABLE DISCONNECTED FROM 1JB7667085
90557291 | 2019-12-21 | A081-0S0143B | 0S-0143B HC FILTER REPLACEMENT-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10316614 | 700002202402 | DKME | Integrity | 5757.25 | 27 | 46 |  |  |  |  | 17.09.2019 05:25:46 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-143B HC FILTER IN U-100 STRING-1 MAY REQUIRE FILTER REPLACEMENT WHEN THE RUNNING FILTER GETS EXHAUSTED 17.09.2019 06:03:14 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 17.09.2019 06:04:56 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-143 B HC FILTER IN U-100 STRING-2 REPLACEMENT REQUIRED
90557292 | 2019-12-11 | A081-0S0143B | 0S-0143B HC FILTER REPLACEMENT-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10316615 | 700002202402 | DKME | Integrity | 3720.8 | 27 | 46 |  |  |  |  | 17.09.2019 05:37:15 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-143B HC FILTER IN U-100 STRING-1 MAY REQUIRE FILTER REPLACEMENT WHEN THE RUNNING FILTER GETS EXHAUSTED
90557293 | 2019-10-01 | A081-0S0123A | 0S-0123A FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10316610 | 700002201322 | DKME | Integrity | 1376.76 | 27 | 46 |  |  |  |  | 17.09.2019 05:19:13 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123 A HC FILTER IN U-100 STRING-1 MAY REQUIRE FILTER REPLACEMENT ONCE THE RUNNING ONE GETS EXHAUSTED.
90557294 | 2019-12-21 | A081-0S0123B | 0S-0123B FILTER REPLACEMENT-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10316613 | 700002200643 | DKME | Integrity | 4072.29 | 27 | 46 |  |  |  |  | 17.09.2019 05:24:46 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123B HC FILTER IN U-100 STRING-1 MAY REQUIRE FILTER REPLACEMENT WHEN THE RUNNING FILTER GETS EXHAUSTED.
90557295 | 2019-11-02 | A081-0S0123B | 0S-0123B FILTER REPLACEMENT-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10316612 | 700002200643 | DKME | Integrity | 549.54 | 27 | 46 |  |  |  |  | 17.09.2019 05:22:16 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123 B HC FILTER REPLACEMENT IN U-100 STRING-1 MAY REQUIRE WHEN THE RUNNING FILTER GETS EXHAUSTED
90558262 | 2019-09-24 | A081-1S0241 | 1S-0241 FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10317325 | 700002354895 | JFC CORPORATION | Integrity | 1248.97 | 22 | 61 |  |  |  |  | 24.09.2019 08:36:28 UTC Prashant Tamhane (QRPTA0) 1S-0241 DP is in increasing trend need to replace filter element. PEFS: T-13.370.089 Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. HIgh DP could buckeled the filter. What actions did you already take to solve the problem, share information. Current DP is 1.2 barg. Proactively raised notification as we have to isolate the filter once DP reach 1.8barg ICC Required
90558823 | 2019-10-07 | A081-2A8324 | TR2 DAF SCRAPPER SMALL WHEEL DAMAGE FO1 | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10317622 | 700002297332 |  | Integrity | 255.56 | 70 | 70 | Normal Wear | Normal Wear-Lining damage | Bund / bunded area | Fix / Repair | 28.09.2019 01:15:34 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. TR2 DAF scrapper small wheel damage, to be replaced before getting bad and damaging the run way PEFS: T-4.118.867 Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : Bagus Phone : 44032215 08.10.2019 10:32:04 UTC Kolappan Ramalingom Asari (QRKRA0) Damage small whell removed out, New whell replaced, job completed, sap closed.
90558850 | 2019-11-24 | A081-0S0163B | 0S-0163B FILTER DP HIGH NEED TO REPLACE | MX04 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10317584 | 700002200043 | DKME | Integrity | 19378.87 | 27 | 46 |  |  |  |  | 26.09.2019 19:16:19 UTC Sivakumar Manokaran (QRSMAA) 0S-0163B filter DP high need to repalce the filter element
90559642 | 2019-10-03 | A081-1S0241 | 1S-0241 FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10318067 | 700002354895 | JFC CORPORATION | Integrity | 1082.07 | 22 | 60 |  |  |  |  | 02.10.2019 07:34:21 UTC Prashant Tamhane (QRPTA0) 1S-0241 DP is in increasing trend need to replace filter element. PEFS: T-13.370.089 Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. HIgh DP could buckeled the filter. What actions did you already take to solve the problem, share information. Current DP is 1.4 barg. Proactively raised notification as we have to isolate the filter once DP reach 1.7barg
90560521 | 2019-11-18 | A081-2SB210N2 | BB AREA FAULTY LAMPS REPLACEMENT ACTIVIT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10318535 | 700002373562 | ABB MALAYSIA | Electrical | 6754.93 | 60 | 115.1 | end of life | end of life- | Lamps |  | 08.10.2019 08:00:10 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90554409)FOUND MANY LAMPS ARE NOT WORKING AT U3000 PIPERACK, REACTORS SIDE, EXCHANGER SIDE, FIN FAN <(>&<)> COMPRESSOR AREAS AND U3400 AREA.AND SEE ATTACHED DOCUMENT FOR REFERANCE. 1)2x36W LIGHT FITTING LAPMS--120 No's) 2)2X18W LIGHT FITTING LAPMS- 50 No's) PEFS: Prioriteit: Additional mitigations : X Scaffold--MOBILE SCAFFOLDING REQUIRED IN BELOW THE MAIN PIPERACK AND REMAINING AREA WILL DO BY 'A' TYPE LADDER. Electrical tasks: X E-isolation X JHA needed Requester Name : VASIM
90560524 | 2019-11-06 | A081-2SB210N2 | BB AREA LIGHT FITITING DIFFUSERS DAMAGED | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10318538 | 700002373562 | ABB MALAYSIA | Electrical | 1099.96 | 8 | 8 | Mechanical damage | Mechanical damage- | Lighting Fixture |  | 08.10.2019 08:13:43 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. AS PER PM WO# 90554408, VISUAL INSPECTION MADE AND REFER FOR OBSERVATION IN ATTACHED QAQC, EX INTEGRITY RELATED SYMPTOMS. 1) 18W DIFFUSER FAILED- 2 PCs TO BE REPLACED 2) 36W DIFFUSER FAILED- 4 PCs TO BE REPLACED TAG NO'S- 1) 2LFN210N226L210 2)2LFN210N224L303, 3)2LFE210E101L312, 4) 2LFE210E101L131--36W DIFFUSERS 1) 2LFN210N215L105, 2) 2LFN210N210L203--18W DIFFUSERS (FOR ACCESS WE WILL DO BY 'A' TYPE LADDER) PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : VASIM Phone : 44032804
90560533 | 2019-10-16 | A081-1S0241 | 1S-0241 DP INCREASING TREND,FILTER REPLA | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10318566 | 700002354895 | JFC CORPORATION | Integrity | 1022.75 | 22 | 60 |  |  |  |  | 08.10.2019 18:00:54 UTC Antony Elvin Wilson (QRAWI1) 1S-0241 DP is in increasing trend need to replace filter element. PEFS: T-13.370.089 Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. HIgh DP could buckeled the filter. What actions did you already take to solve the problem, share information. Current DP is 1.4 barg. Proactively raised notification as we have to isolate the filter once DP reach 1.7barg
90561164 | 2019-12-22 | A081-2SB210N2 | BB_BUSTED 400W LAMPS REPLACEMENT (CRANE) | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10318596 | 700002373562 | ABB MALAYSIA | Electrical | 3458.13 | 48 | 66.1 | end of life | end of life- | Lamps |  | 09.10.2019 06:02:42 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. AS PER PM WO# 90554409, FOUND BB ABOVE REACTORS_2R-3021 TO 3029 AREA- CRANE TOP SIDE 400W LIGHTS FAULTY, NEED TO TROUBLESHOOT/ LAMP REPLACEMENT. SEE BELOW TAG NO'S. 1)2LFN210N214L114, 2)2LFN210N214L213, 3)2LFN210N214L220, 4)2LFN210N214L115, 5)2LFN210N214L312, 6)2LFN210N214L214, 7)2LFN210N215L212, 8)2LFN210N215L111, 9)2LFN210N216L113, 10)2LFN210N216L114 PEFS: T-4.013.093, 098, 103 Prioriteit: Additional mitigations : X Scaffold (REQUIRED ON CRANE PLATFORM 1MTR) Electrical tasks: X E-isolation (PERSONAL ISOLATION) X JHA needed Requester Name : VASIM Phone : 44032804 MATERIAL-10650783-10 No's, 10650771-4 No's, 10650567-2 No's
90562103 | 2019-10-26 | A081-1SB210N2 | Poor Lighting in 1R- 3027 Area | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10319784 | 700002352082 | ABB MALAYSIA | Electrical | 1232.12 | 26 | 32.1 | end of life | end of life- | Lamps | Replace | 21.10.2019 09:42:44 UTC Rohit Kumar Jain (QRRJA1) Clear description of the problem. GTL Train -1 /1R-3027 up coming CCO Reactor area Poor lighting Fist floor S3 <(>&<)> S7 location and Rector Top Floor. 40% area lighting not working. PEFS: Prioriteit: Requester Name : Rohit Kumar Jain Phone : 440323114 28.10.2019 05:51:21 UTC Prabakaran Subramanian (QRPSU8) Phone 44032804 EQ ID CHANGED TO A081-1SB210N2/ 700002352082
90562286 | 2019-11-17 | A081-294XA-50200-S | 2ET-LPU-050_ EHT FAULT;ELEC TRACING CMN | MX04 |  | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10319895 |  |  |  | 320.85 | 61 | 67 | Incorrect setting/calibration | Incorrect setting/calibration- | Heat Tracing | Other - please specify in text field | 22.10.2019 10:21:56 UTC Marikkan Thangavel (QRMTH9) 2ET-LPU-050 heat tracing circuit alarms observed and try reset, Not reseted. At field EHT circuit Transfered from Redundant To Main and alram got RESET. To be check <(>&<)> Rectify Main <(>&<)> Redundant ECM faults alarm, If required need to be replace NEW tested ECM. ECM replacement access on Platform. NOT required scaffolding.
90562649 | 2019-11-03 | A081-1S0241 | 1S241 FILTER ELEMENT REPLACEMENT DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10320740 | 700002354895 | JFC CORPORATION | Integrity | 1569.21 | 22 | 60 |  |  |  |  | 26.10.2019 23:54:34 UTC Sudesh Shetye (QRSSH7) Clear description of the problem. 1A2 U-0200 1S-0241 FILTER DP FOUND HIGH FILTER ELEMENT NEED TO BE REPLACED PEFS: T-13.370.089 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X JHA needed Requester Name : GOVIND Phone : 44032111
90563442 | 2020-12-22 | A081-0S0123B | 0S-0123B FILTER DP HIGH-> | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10321301 | 700002200643 | DKME | Integrity | 3992.96 | 27 | 46
90563615 | 2019-11-10 | A081-FIRE HYDRANT | SCE FH117 winged cam missing | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10321401 |  |  |  | 284.06 | 14 | 14 | Erosion | Erosion-WING CAM BROKEN | Fire water hydrant | Replace | 31.10.2019 10:55:55 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in October 2019 for Water/ETP, it was found that the winged cam assembly on the right side of the two way hydrant was broken off at hydrant FH117. FH117 is located in 7th Avenue opposite Water Pumps. The spare part MM number is 10687723. There are available spare parts in WHS. All details and specifications will be forwarded to OMC. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 11.11.2019 11:45:31 UTC Raj Mohansingh (QRRMOA) SCE FH117 - WINGED CAM MISSING SO INSTALLED NEW ONE, JOB COMPLETED
90563616 | 2019-11-10 | A081-FIRE HYDRANT | SCE FH107 winged cam missing | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10321399 |  |  |  | 284.06 | 14 | 14 | Erosion | Erosion-WING LOCK ASSAMBALY BROKEN | Fire water hydrant | Replace | 31.10.2019 10:49:49 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in October 2019 for Water/ETP, it was found that the winged cam assembly was broken off at hydrant FH107. FH107 is located in Road E opposite Fire Pumps. The P<(>&<)>ID number is FH2-5. The spare part MM number is 10687723. There are available spare parts in WHS. All details and specifications will be forwarded to OMC. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 11.11.2019 11:35:18 UTC Raj Mohansingh (QRRMOA) SCE FH107 - WINGED CAM MISSING SO INS5TALLED NEW ONE, HOUSEKEEPING DONE JOB COMPLETED
90563797 | 2019-11-18 | A081-2A8324 | DAF-2 SMALL ARM SCUM PLATE L-ANGLE RUBBI | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP |  | 700002297332 |  | Integrity | 0 | 0 | 0
90563810 | 2019-11-04 | A081-2A8324 | DAF-2 SMALL ARM SCUM PLATE L-ANGLE RUBBI | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10321603 | 700002297332 |  | Integrity | 59.85 | 36 | 36 | Normal Wear | Normal Wear- | Rotating element | Fix / Repair | 03.11.2019 11:24:04 UTC Srinivasan Ramasamy (QRSRAE) Clear description of the problem. DAF-2 SCRAPPER SMALL WHEEL ARM SCUM PLATE "L" ANGLE RUBBING WITH SCUM TROUGH GUIDE VANE PEFS: T-4.118.867 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. IT MAY DAMAGE SCUM TROUGH OR SCRAPPER X JHA needed Requester Name : SRINIVASAN RAMASAMY Phone : 44032215
90563948 | 2019-12-02 | A081-0S0163A | 0S-0163A HC FILTER REPLACEMENT. | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10321686 | 700002200042 | DKME | Integrity | 2185.83 | 27 | 46 |  |  |  |  | 04.11.2019 13:39:34 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163 A HC FILTER REPLACEMENT NEED TO BE DONE ONCE IT EXHAUSTS.
90564045 | 2019-11-30 | A081-294XA-50200-S | TR2 MB EHT CMN FAULT ALARM | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10321716 | 700002607282 |  | Instrumentation | 0 | 4 | 6 | Incorrect setting/calibration | Incorrect setting/calibration- | Heat Tracing | Other - please specify in text field | 05.11.2019 01:21:57 UTC Ayaz Khan Khan (QRAMU3) Clear description of the problem. 294XA50200 ELEC TRACING CMN FAIL ALARM, TO BE ATTEND PEFS: XXXXX Prioriteit: Additional mitigations : X JHA needed Requester Name : AYAZ KHAN Phone : 44032413 30.11.2019 12:30:03 UTC Premkumar Dayalan (QRPDA2) Phone 70483989 Initial check done. Notification already for rectification - 90565900 / 10323120.
90564054 | 2019-12-07 | A081-FIRE HYDRANT | CLARIFIER TR1 A OPPSITE FIRE HYDRANT 144 | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10321273 |  |  |  | 176.86 | 8 | 8 |  |  |  |  | 31.10.2019 00:14:31 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. CLARIFIER TR 1 A OPPOSITE FIRE HYDRANT FIELD TAG NUMBER FH-144 ,BOTH FH NOZZLE WORNOUT ,FIRE HOSE UNABLE TO FIX FOR CLARIFIER V NOUCH CLEANING.TO BE FIXED.PEFS ATTACHED FOR REFERENCE. PEFS: T-4.118.464 Prioriteit: Additional mitigations : Requester Name : RAJA RAMASAMY Phone : 44032215 07.12.2019 15:35:53 UTC Madhan Subramani (QRMSUA) Removed old wing nut for two side and replace new wing nut.job completed.
90564091 | 2020-02-12 | A081-2SB200N2 | BA AREA FAULTY 36w/18w LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10321809 | 700002373557 | ABB MALAYSIA | Electrical | 4542.42 | 54 | 79 | end of life | end of life- | Lamps | Replace | 06.11.2019 07:05:27 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90555397)FOUND MANY LAMPS ARE NOT WORKING AT U23100,U23200,MAIN PIPERACK, REACTORS SIDE, EXCHANGER SIDE, FIN FAN <(>&<)> COMPRESSOR HOUSE AREA.SEE ATTACHED DOCUMENT FOR REFERANCE. 1)2x36W LIGHT FITTING LAPMS--100 No's) 2)2X18W LIGHT FITTING LAPMS- 30 No's) PEFS: Prioriteit: Additional mitigations : X Scaffold --MOBILE SCAFFOLDING REQUIRED IN BELOW THE MAIN PIPERACK AND REMAINING AREA WILL DO BY 'A' TYPE LADDER. Electrical tasks: X E-isolation X JHA needed Requester Name : VASIM
90564092 | 2019-12-19 | A081-2SB200N2 | BA_BUSTED 400W LAMPS REPLACEMENT ACTIVIT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10321810 | 700002373557 | ABB MALAYSIA | Electrical | 1745.04 | 56 | 297 | end of life | end of life- | Lamps |  | 06.11.2019 07:18:08 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90555397)FOUND MANY FLOOD LIGHTS (400W) ARE NOT WORKING AT ALL AREA. NEED TO TROUBLESHOOT/LAMP RE PLACEMENT. SEE BELOW TAG NUMBERS. 1) 2LFN200N215L315 2) 2LFN200N204L306 3) 2LFN200N205L219 4) 2LFN200N205L319 5) 2LFN200N205L306 6) 2LFN200N207L202 7) 2LFN200N207L101 8) 2LFN200N201L219 9) 2LFN200N240L201 PEFS: T-4.013.068, 71, 79, 74, 72, 85, 77 Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : VASIM Phone : 44032804 MATERIAL; 10650783-- 9 No's, 10650567-2 No's, 10650771--4 No's
90564093 | 2020-01-23 | A081-2SB200N2 | BA_BUSTED 250W/150W LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10321813 | 700002373557 | ABB MALAYSIA | Electrical | 709.83 | 64 | 366.5 | end of life | end of life- | Lamps |  | 06.11.2019 07:30:32 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90555397)FOUND MANY FLOOD LIGHTS (250W / 150W) ARE NOT WORKING AT ALL AREA. NEED TO TROUBLESHOOT/LAMP REPLACEMENT. SEE BELOW TAG NUMBERS. 250W FLOOD LIGHTS: 1)2LFN200N203L107 2)2LFN200N203L209 3)2LFN200N203L308 4)2LFN200N213L204 5)2LFN200N202L213 6)2LFN200N219L316 150W FLOOD LIGHTS :1)2LFN200N206L111 2)2LFN200N205L314 3)2LFN200N214L114 PEFS: T-4.013.064, 458, 457, 072, 085, 078, 063 Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : VASIM Phone : 44032804
90565012 | 2020-12-09 | A081-294XA-50200-S | PMFLT:247RV-10001 REPLACE EHT CABLE | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10322569 | 700002607282 |  | Instrumentation | 71.18 | 25 | 45 | Loss of Heating | Loss of Heating-MIQ heater cable opened | Heat Tracing | Disconnect / Reconnect
90565456 | 2019-11-15 | A081-0S0163B | 0S-0163B filter DP high : OPS REQST | MX04 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10322841 | 700002200043 | DKME | Integrity | 302.31 | 27 | 46 |  |  |  |  | 13.11.2019 22:54:04 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0163B filter exhausted and filter element to be replaced. PEFS: Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. 0S-0163A taken in service Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90565900 | 2019-12-31 | A081-294XA-50200-S | 2ET-LDF-002_ EHT FAULT;ELEC TRACING CMN | MX04 |  | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10323120 |  |  |  | 4425.53 | 64 | 210 | Incorrect setting/calibration | Incorrect setting/calibration-ECM and RTD malfunction | Heat Tracing | Field repair | 17.11.2019 06:15:58 UTC Sivaramakrishnan Krishnapandi (QRSKR4) During inspection found the EHT circuit alarm came frequently,need to rectify the alarm Note: Insulation removal and scaffold not required
90566388 | 2019-11-23 | A081-0S0163A | 0S-163A filter element to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10323485 | 700002200042 | DKME | Integrity | 0 | 27 | 46 |  |  |  |  | 20.11.2019 20:04:18 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-163A filter element to be replace. P-1 pigging is due to filter choking frequency may increase. PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. S/By filter to be taken online. Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90566390 | 2019-12-21 | A081-0S0163A | 0S-0163A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10323486 | 700002200042 | DKME | Integrity | 500.96 | 27 | 46 |  |  |  |  | 20.11.2019 20:07:02 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-163A filter element to be replace. P-1 pigging is due to filter choking frequency may increase. PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. S/By filter to be taken online. Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90566391 | 2019-12-05 | A081-0S0163B | 0S-0163B FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10323487 | 700002200043 | DKME | Integrity | 14737.7 | 27 | 46 |  |  |  |  | 20.11.2019 20:09:24 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-163B filter element to be replace. P-1 pigging is due to filter choking frequency may increase. PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. S/By filter to be taken online. Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90566392 | 2019-01-01 | A081-0S0163B | 0S-0163B FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10323489 | 700002200043 | DKME | Integrity | 3842.79 | 46 | 46 |  |  |  |  | 20.11.2019 20:14:37 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-163B filter element to be replace. P-1 pigging is due to filter choking frequency may increase. PEFS: T-4.094.342 Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. S/By filter to be taken online. Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115 PEFS: T-4.094.342
90566393 | 2019-11-30 | A081-0S0123A | 0S-123A filter element to be replace | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10323479 | 700002201322 | DKME | Integrity | 4183.14 | 27 | 46 |  |  |  |  | 20.11.2019 19:58:00 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-123A filter element to be replace. P-1 pigging is due to filter choking frequency may increase. PEFS: T-13.370.023 Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. S/By filter to be taken online. Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90566394 | 2019-12-21 | A081-0S0123A | 0S-0123A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10323482 | 700002201322 | DKME | Integrity | 366.38 | 27 | 46 |  |  |  |  | 20.11.2019 19:59:50 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-123A filter element to be replace. P-1 pigging is due to filter choking frequency may increase. PEFS: T-13.370.023 Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. S/By filter to be taken online. Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90567435 | 2020-10-01 | A081-0P2021 | ASU-PROCURE ACC CLEANING HOSE FOR 0P2021 | MX09 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10324034 | 700002199414 | PRATISSOLI | Rotating | 25098.45 | 0 | 0 |  |  |  |  | 26.11.2019 12:17:06 UTC Darius Martin (QRDMA2) Clear description of the problem. ASU Train 1 - Procure ACC cleaning discharge hoses for pump 0P-2021. PEFS: Prioriteit: Additional mitigations : Requester Name : DARIUS MARTIN Phone : 44032213
90568182 | 2020-02-02 | A081-0S0123A | 0S-0123A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10324471 | 700002201322 | DKME | Integrity | 268.58 | 27 | 46 |  |  |  |  | 29.11.2019 08:59:32 UTC Elangovan Muthusamy (QREMU0) 0S-123A DP high filter element to be replaced
90569245 | 2021-08-29 | A081-0S0163A | EHT/insulation reposition refit 0S0163A- | MX04 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10325217 | 700002200042 | DKME | Integrity | 944.48 | 14 | 96 |  |  |  |  | 05.12.2019 08:58:39 UTC MICHAEL Michael George (QRMVE0) Clear description of the problem. *EHT (electrical heat tracing cable) exposure without insulation in 0S-0163A top cover bolts area. *EHT cable can damage while doing the filter element replacement, top cover bolts opening job. *Filter top cover insulation cladding damaged and exposure to atmosphere. *Electrocution hazard. Job no 1: EHT along require repositioning on the top cover bolts area. Job no 2: *Insulation need to re-install in the spectacle spade area *Insulation with cladding on the filter body near top flange bolts need to reposition along with EHT. *top cover insulation jacket requires for easy handling while job PEFS: T-4.094.342 Prioriteit: Additional mitigations : Requester Name : Michael Phone : 44032115
90569246 | 2021-01-28 | A081-0S0163B | EHT/insulation reposition refit 0S0163B- | MX04 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10325221 | 700002200043 | DKME | Integrity | 1291.1 | 0 | 104
90569252 | 2021-09-11 | A081-0S0143A | EHT/insulation reposition refit 0S0143A- | MX04 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10325215 | 700002201324 | DKME | Integrity | 1278.76 | 12 | 75
90570167 | 2020-01-06 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10325818 | 700002200042 | DKME | Integrity | 566.42 | 27 | 46 |  |  |  |  | 12.12.2019 13:50:56 UTC Sivakumar Manokaran (QRSMAA) 0S-0163A filter DP high need to repalce the filter element.
90570694 | 2020-01-25 | A081-0S0163B | 0S-0163B FILTER CHOKE NEED TO CLEAN | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10326116 | 700002200043 | DKME | Integrity | 25227.69 | 27 | 46 |  |  |  |  | 17.12.2019 09:53:57 UTC Sivakumar Manokaran (QRSMAA) U-0100 String-3 Hydro carbon filter 0S-0163B filter choke need to be cleaned.
90570697 | 2019-12-23 | A081-1S0241 | 1S-0241 element needs to be replaced. | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10326022 | 700002354895 | JFC CORPORATION | Integrity | 1218.32 | 22 | 60 |  |  |  |  | 16.12.2019 10:31:21 UTC Pratik Manilal Prajapati (QRPPR1) 1S-0241 filter element to be replaced as it is suspected channeling happened inside the filter. PEFS: T-13.370.089 Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Filter DP was reducing during increased load and TSS content increased in the solvent. What actions did you already take to solve the problem, share information. Current DP is 0.5 barg. As per technologist need to replace the element with 5 micron.
90570820 | 2019-12-26 | A081-2A8324 | TR-2 DAF SCRAPPER PLATE BOLTS TO FIX | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10326337 | 700002297332 |  | Integrity | 650.48 | 108 | 108 | Other - please specify in text field | Other - please specify in text field- | Other - please specify in text field | Fix / Repair | 18.12.2019 13:47:42 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. TR-2 DAF SCRAPPER PLATE RUBBER PORTION SOME OF THE BOLTS ARE MISSING TO BE PROVIDED PEFS: T-4.118.867 Prioriteit: Additional mitigations : Requester Name : CIFAS JEYAKARAN Phone : 44032215
90571176 | 2019-12-24 | A081-2A8324 | 2A8324 small wheel to be replaced | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10326601 | 700002297332 |  | Integrity | 881.09 | 0 | 18 | Other - please specify in text field | Other - please specify in text field-wheel damage | Other - please specify in text field | Replace | 23.12.2019 00:35:59 UTC Mohanraj Chellaih (QRMCH0) Clear description of the problem. TR2 DAF scrapper small wheel bearing damage. Wheel showing wobble while moving PEFS: T-4.118.867 Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation Requester Name : Baskar Phone : 44032215 24.12.2019 09:04:21 UTC Arunbhai Patel (QRAPA0) Removed damage wheel and replaced new two set and fixed back.
90571948 | 2019-12-30 | A081-0S0123A | 0S123A FILTER ELEMENT TO BE REPLACE OPS | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10326974 | 700002201322 | DKME | Integrity | 0 | 0 | 0 |  |  |  |  | 29.12.2019 09:04:02 UTC Balakrishna Guthu Mijar (QRBMI0) 0S123A FILTER ELEMENT TO BE REPLACE AS PIGGING IS SCHEDULED ON 30/12/2019 29.12.2019 11:33:00 UTC Bakthavatchalan Thenral (QRBTH0) ICC is live
90572100 | 2019-12-31 | A081-0X0104 | Dr.M.Filter conveyor glass broke OPS-> | MX04 | M_PAC_CON2 | Routine Wrk Lvl 4 | 0 |  | SCREW CONVEYOR | CM | FGP | 10326984 | 700002206193 |  | Electrical | 0 | 8 | 7 | Normal Wear | Normal Wear-Due to operational issues | guards/doors | Cleaned | 29.12.2019 12:10:42 UTC Suresh Babu Narayanan (QRSNA7) Dr.M.Filter 0X-104 conveyor view glass broken due to cellose material bulging. We cannot procede further for the Dr.M.Filter Batch filter processing. 30.12.2019 07:11:48 UTC Bakthavatchalan Thenral (QRBTH0) ICC required, PIGGING is planned today, for processing water this coveyor is required
90572449 | 2020-02-05 | A081-294XA-50200-S | 2ET-LPU-090_ EHT FAULT;ELEC TRACING CMN | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10326824 | 700002607282 |  | Instrumentation | 3949.55 | 46 | 168 | Loss of Heating | Loss of Heating-thermostat failed | Heat Tracing | Hardware Replacement | 26.12.2019 04:28:43 UTC Marikkan Thangavel (QRMTH9) Clear description of the problem. During inspection found the EHT circuit alarm came frequently, need to rectify the alarm BY check RTD,ECM function. and if required replace. Note: Insulation removal required after trouble shooting. * scaffolding REQUIRED PEFS: PEFS: Prioriteit: Additional mitigations : Electrical tasks: Requester Name : MARIKKAN Phone : 66853577
90572453 | 2020-02-20 | A081-294XA-50200-S | 2ET-LPU-050_ EHT FAULT;ELEC TRACING CMN | MX04 |  | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10326823 |  |  |  | 4023.95 | 49 | 136 | Loss of Heating | Loss of Heating-thermostat failed | Heat Tracing | Hardware Replacement | 26.12.2019 04:18:16 UTC Marikkan Thangavel (QRMTH9) Clear description of the problem. During inspection found the EHT circuit alarm came frequently, need to rectify the alarm BY check RTD,ECM function. and if required replace. Note: Insulation removal required after trouble shooting. * scaffolding NOT REQUIRED PEFS: Prioriteit: Additional mitigations : Electrical tasks: Requester Name : MARIKKKAN Phone : 66853577
90572634 | 2020-01-09 | A081-0S8361A | 0S8361A BELLOW LEAK LIQUOR SIDE | MX04 | M_ROT_CENT | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10327453 | 700001729713 |  | Rotating | 3322.86 | 27 | 27 | Normal Wear | Normal Wear- | Other - please specify in text field | Other - please specify in text field | 31.12.2019 21:29:13 UTC Vasu Sampathkumar (QRVSA0) Clear description of the problem. 0S8361A CENTRIFUGE CENTRATE LIQOUR SIDE BELLOW DAMAGED CONDITION. PEFS: T-4.253.274 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X JHA needed Requester Name : JAYKUMAR Phone : 44032215 13.01.2020 12:30:30 UTC Weston Thampy (QRWTH0) BELLOW REPLACED WITH NEW
90572782 | 2020-01-16 | A081-0S0123B | 0S-0123B HC FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10327571 | 700002200643 | DKME | Integrity | 0 | 27 | 46 |  |  |  |  | 01.01.2020 12:23:05 UTC Sunil Kumar Puliyath (QRPSU4) Clear description of the problem. Str # 1 Hydrocarbon filter 0S-0123B filter element need to replace with new filter. PEFS: T-13.370.023 Prioriteit: Additional mitigations : Requester Name : P Sunil Phone : 44032115 02.01.2020 09:49:59 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90574547 | 2020-01-20 | A081-1S0241 | 1S-0241 ELEMENT NEEDS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10328254 | 700002354895 | JFC CORPORATION | Integrity | 1070.32 | 22 | 60 |  |  |  |  | 10.01.2020 20:24:13 UTC Pratik Manilal Prajapati (QRPPR1) Clear description of the problem. 1A2 U-0200 1S-0241 FILTER DP FOUND HIGH FILTER ELEMENT NEED TO BE REPLACED PEFS: T-13.370.089 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X JHA needed Requester Name : YOUCEF Phone : 44032111
90575054 | 2020-02-25 | A081-1F5111 | HW-1F5111 BNR E8 TIP WELD CORROSN;REPLC | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10328570 | 700002348459 | KTI | Integrity | 205.55 | 40 | 50 | Material defect | Material defect-Plug welding defect | Burner - cup throat | Replace | 14.01.2020 09:47:21 UTC Velmurugan Subramanian (QRVSU0) 1F5111 BURNER E8 TIP FOUND WELDING CORROSION. TIP NEEDS REPLACEMENT.PHOTO ATTACHED
90575219 | 2020-02-02 | A081-0S0163B | 0S-0163B FILTER CHOKE NEED TO CLEAN | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10328730 | 700002200043 | DKME | Integrity | 3867.75 | 27 | 46 |  |  |  |  | 16.01.2020 00:05:38 UTC Sivakumar Manokaran (QRSMAA) 0s-0163B HC FILTER DP HIGH NEED TO REPLACE THE FILTER ELEMENT 16.01.2020 04:40:15 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90575562 | 2020-02-25 | A081-1F5111 | HW-1F5111 BNR B13 TIP WELD COROSN;JC | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10328852 | 700002348459 | KTI | Integrity | 216.42 | 40 | 50 | Material defect | Material defect-Plug welding defect | Burner - cup throat | Replace | 16.01.2020 11:43:11 UTC Velmurugan Subramanian (QRVSU0) 1F-5111 BURNER B13 TIP FOUND WELDING CORROSION.IT REQUIRES REPLACEMENT. PHOT ATTACHED FOR REFERENCE.
90575565 | 2020-02-08 | A081-1F5111 | HW-1F5111 BNR E4 TIP DAMAGE; REPLACE; | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10328851 | 700002348459 | KTI | Integrity | 0 | 38 | 50 |  | - | Other - please specify in text field |  | 16.01.2020 11:40:11 UTC Velmurugan Subramanian (QRVSU0) 1F-5111 BURNER E4 TIP FOUND WELDING CORROSION. IT REQUIRES TIP REPLACEMENT. PHOTO ATTACHED FOR REFERENCE
90575574 | 2020-02-08 | A081-1F5111 | HW-1F5111 BNR D15 TIP CRACK;REPLC | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10328676 | 700002348459 | KTI | Integrity | 0 | 35 | 50 |  | - | Burner - cup throat |  | 15.01.2020 10:57:42 UTC Velmurugan Subramanian (QRVSU0) 1F5111 Burner B10 tip having crack- Needs Replacement . Photo attached 18.02.2020 08:59:09 UTC Vijay Paramasivam (QRVPA3) Phone 44032637 IGNORE ABOVE BNR TAG NUMBER;ACTUAL TAG NUMBER IS D-15; WO IS FOR BNR D-15 TIP REPLACEMENT.
90575590 | 2020-02-02 | A081-294XA-50200-S | 2ET-LPU-88 EHT TRBLSHOOT&REPLC IF REQ | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10328781 | 700002607282 |  | Instrumentation | 4162.4 | 199 | 168 | Loss of Heating | Loss of Heating-thermostat failed | Heat Tracing | Hardware Replacement | 16.01.2020 07:31:35 UTC Premkumar Dayalan (QRPDA2) Phone 70483989 Clear description of the problem. Panel operator informed that EHT common alarm existing in panel, checked and found 2ET-LPU-88 found tripped. Checked and changed the circuit from Main to Returdant. Now working normal, Main circuit need to check the ECM and thermostat for proper functioning and replace if required. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : PREMKUMAR Phone : 70483989
90576313 | 2020-01-28 | A081-0S0143B | 0S-0143B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10329385 | 700002202402 | DKME | Integrity | 218.5 | 27 | 48 |  |  |  |  | 22.01.2020 23:40:53 UTC Sivakumar Manokaran (QRSMAA) 0S-0143B Hydro Carbon filter DP high need to replace the fitler element.
90576758 | 2020-01-27 | A081-0S0163A | 0S0163A filter DP high- Str-2 SD PRD OPS | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10329727 | 700002200042 | DKME | Integrity | 160.57 | 27 | 48 |  |  |  |  | 27.01.2020 06:49:29 UTC Sivakumar Manokaran (QRSMAA) 0S-0163A filter DP high need to repalce the fitler elements
90576911 | 2020-02-05 | A081-2A8324 | DAF-2 SCRAPPER BRIDGE SMALL WHEEL DAMAGE | MX04 | M_X_X | Emergency | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10329603 | 700002297332 |  | Integrity | 0 | 20 | 60 | Normal Wear | Normal Wear- | Bearing | Replace | 25.01.2020 14:02:38 UTC d Pwambok (QRDPW0) FLOTATOR PACKAGE NDE BEARING SLIGHT DAMAGE OBSERVED PEFS: Prioriteit: Additional mitigations : X Scaffold X LOTO/Spading Electrical tasks: X E-isolation X JHA needed Requester Name : DAVID Phone : 44032215 29.01.2020 04:49:27 UTC Raju Sutham (QRRSU3) THIS NOTIFICATION CONVERTED TO EMERGENCY DUE SCRAPPER ARM TWO NUMBERS OF SMALL WHEEL DAMAGED, NEED TO REPLACED ON EMERGENECY BASIS. DAF IS SHUT DOWN CONDITION. 29.01.2020 10:46:43 UTC Yogarajan Pandiyan (QRYPA0) Small rollers replaced : Permit No 1256179
90577780 | 2020-02-04 | A081-1S0241 | 1S-0241 ELEMENT NEEDS TO BE PREPARED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10330100 | 700002354895 | JFC CORPORATION | Integrity | 1374.24 | 0 | 60 |  |  |  |  | 01.02.2020 00:13:08 UTC Pratik Manilal Prajapati (QRPPR1) 1A2 U-0200 1S-0241 FILTER DP FOUND HIGH FILTER ELEMENT NEED TO BE REPLACED PEFS: T-13.370.089 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X JHA needed Requester Name : PRATIK
90577781 | 2020-02-16 | A081-0S0123A | 0S-0123A FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10330029 | 700002201322 | DKME | Integrity | 17918.68 | 46 | 46 |  |  |  |  | 30.01.2020 14:09:25 UTC Balakrishna Guthu Mijar (QRBMI0) 0S-0123A Filter elements to be replaced
90577889 | 2020-03-04 | A081-1SB210N2 | AB_ 36W & 18W FAULTY LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330306 | 700002352082 | ABB MALAYSIA | Electrical | 6451.36 | 36 | 189 | end of life | end of life- | Lamps |  | 02.02.2020 08:11:34 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING AB AREA LIGHTING PM FOUND 36W <(>&<)> 18W FLOUROCENT LIGHTING FIXTURE NOT WORKING NEED TO REPAIRE, CORRECT OR REPLACE.SEE ATTACECHED SHEET FOR FAULT LIGHTING FIXTURE. PEFS: Prioriteit: X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : SHYAM TIWARI Phone : 4403 2804 13.02.2020 11:36:43 UTC Mohammad Alam (QRMANR) As discussed with electrical team, only Accessable light to be execute by this wo. remaing will be done separate wo with scaffolding. 15.03.2020 09:31:52 UTC Sudheer Kumar Pendurthi (QRSPE6) We raised new notification: 10333722 for 36w lamps repalcement
90577890 | 2020-02-29 | A081-1SB210N2 | AB_250W LFT NEED TO TROUBLESHOOTING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330303 | 700002352082 | ABB MALAYSIA | Electrical | 119.88 | 16 | 120 | end of life | end of life- | Lamps | Replace | 02.02.2020 07:50:22 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING AB AREA LIGHTING INSPECTION BELOW MENTIONED 250W LIGHT NOT WORKING NEED TO RECTIFY NEER 1E-3037<(>&<)>1E-3012. 1LFN210N209L206, 1LFN210N207L312 PEFS: Prioriteit: X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : SHYAM TIWARI Phone : 4403 2804 13.02.2020 12:24:51 UTC Mohammad Alam (QRMANR) pef: T-4.013.347 <(>&<)> T-4.013.439 SF : 5MTR BOTH LIGHT
90577893 | 2020-10-12 | A081-1SB210N2 | AB-FAULTY LAMP REPLACEMENT 150W | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330302 | 700002352082 | ABB MALAYSIA | Electrical | 218.27 | 64 | 480 | end of life | end of life- | Lamps |  | 02.02.2020 07:38:09 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING AB AREA LINGHTING INSPECTION FOUND 150W LAMP FAULTY NEED TO RECTIFY TAG NO. MENTIONED BELOW. 1LFN210N204L104,1LFN210N224L110, 1LFN210N224L210,1LFN210N226L105,1LFN210N226L205,1LFN210N226L103 ,1LFN210N226L203,1LFN210N219L306,1LFN210N219L207 PEFS: Prioriteit: X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : SHYAM TIWARI Phone : 4403 2804
90577896 | 2020-04-14 | A081-1SB210N2 | AB_400W FLT TROUBLESHOOTING ACTIVITY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330299 | 700002352082 | ABB MALAYSIA | Electrical | 531.91 | 26 | 274 | end of life | end of life- | Lamps |  | 02.02.2020 07:22:35 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING AB AREA PM ACTIVITY FOUND 400W LIGHTS NOT GLOWING NEED TO RECTIFY. LIGHTING TAG NO. BELOW MENTION. 1LFN210N204L104,1LFN210N24 1L302, 1LFN210N206L112, 1LFN210N218L106,1LFN210N218L207, 1LFN210N227L108, 1LFN210N2L206, 1LFN210N227L207,1LFN210N227L107, 1LFN210N218L306, PEFS: Prioriteit: X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : SHYAM TIWARI Phone : 4403 2804 16.02.2020 09:40:55 UTC Sudheer Kumar Pendurthi (QRSPE6) 1LFN210N2L206 THIS TAG NO.IS WRONG, CORRECT TAG NO 1LFN210N218L206 16.02.2020 10:21:49 UTC Sudheer Kumar Pendurthi (QRSPE6) 1LFN210N206L112 THIS IS 36W NO NEED TO PLAN. AND INCLUDE THIS TAG NO. 1LFN210N241L201 17.04.2020 11:36:29 UTC Sudheer Kumar Pendurthi (QRSPE6) New notification raised (10336385) for remaining 7 no's 400w lamps repalcement in compressor house.(Why because 1X-3002 crane safety switch
90578132 | 2020-02-08 | A081-2SB210N2 | FS-2R-3023 ELECTRICAL LIGHTING TO CHECK | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10330399 | 700002373562 | ABB MALAYSIA | Electrical | 95.61 | 6 | 4 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 03.02.2020 06:36:33 UTC Ramu Bommana (QRRBO3) Clear description of the problem. 2R-3023 ELECTRICAL LIGHTING TO BE CHECKED AT ALL FLOOR LEVELS FOR ENOUGH LIGHTING. CCO/ROR SPADING AND DESPADING ACTIVITIES ARE AT RISK OR CONCERN DUE TO POOR LIGHTING AT REACTOR FLOOR LEVELS. DAMAGED OR FUSED LIGHTS ARE TO RECTIFIED. PEFS: T-4.002.457 Prioriteit: X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : RAMU BOMMANA Phone : 44032311 04.02.2020 04:38:59 UTC Sankaran Kutty Marar Muraleedharan (QRSMU4) RESET INCASE OF BREAKER TRIP
90578299 | 2020-02-06 | A081-0P2021 | ASU-6 ,ACC ClLEANING PUMP MAINTENANCE | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10330580 | 700002199414 | PRATISSOLI | Rotating | 302.64 | 24 | 0 |  |  |  |  | 05.02.2020 10:15:44 UTC Sudeep Thapliyal (QRSTH8) Clear description of the problem. 1-Multiple leak found from pump suction line need to repaired. 2- Another leak found from Pump discharge line connector PEFS: Prioriteit: Additional mitigations : Requester Name : SUDEEP Phone : 30974437 11.02.2020 05:27:47 UTC Tites Peter (QRTPE0) Elbow repaired by welding. All leaking joints tightened.
90578418 | 2020-02-22 | A081-0S0163A | 0S-0163A FILTER ELEMENT TO BE REPLACEMEN | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10330631 | 700002200042 | DKME | Integrity | 327.77 | 27 | 46 |  |  |  |  | 06.02.2020 08:03:39 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. CONDENSATE FILTER 0S-0163A FILTER ELEMENT TO BE REPLACEMENT. PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. COULDN'T PROCESS CONDENSATE Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90578420 | 2020-03-18 | A081-0S0143A | 0S-0143A FILTER ELEMENT TO BE REPLACEMEN | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10330628 | 700002201324 | DKME | Integrity | 169.55 | 46 | 46 |  |  |  |  | 06.02.2020 07:48:16 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. CONDENSATE FILTER 0S-0143A FILTER ELEMENT TO BE REPLACEMENT. PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. COULDN'T PROCESS CONDENSATE Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90578421 | 2020-05-23 | A081-0S0143B | 0S-0143B FILTER ELEMENT TO BE REPLACEMEN | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10330630 | 700002202402 | DKME | Integrity | 17880.25 | 47 | 47 |  |  |  |  | 06.02.2020 07:51:46 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. CONDENSATE FILTER 0S-0143B FILTER ELEMENT TO BE REPLACEMENT. PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. COULDN'T PROCESS CONDENSATE Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90578621 | 2020-03-16 | A081-1SB220N2 | 1LFN220N206L116 400W LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330657 | 700002356603 | ABB MALAYSIA | Electrical | 45.58 | 8 | 96 | end of life | end of life- | Lamps |  | 06.02.2020 12:43:40 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. FOUND 1 LIGHT 400W 1LFN220N206L116 NOT WORKING DURING LIGHTING INSPECTION NEED TO TROUBLESHOOT. SEE DRAWING T-4.013.358 PEFS: Prioriteit: X Scaffold 10 MTRS HEIGHT Electrical tasks: X E-Disconnect X E-isolation Requester Name : SHYAM TIWARI Phone : 4403 2804
90578624 | 2020-03-12 | A081-1SB220N2 | 1LFN220N230L208 400W NEED TO REPLACE | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330660 | 700002356603 | ABB MALAYSIA | Electrical | 119.74 | 8 | 60 | end of life | end of life- | Lamps | Replace | 06.02.2020 13:05:03 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. 1LFN220N230L208 400W NEED TO REPLACE FOUND FAULTY DURING LIGHTING INSPECTION. SEE DRAWING NO. T-013.0404 8MTR HEIGHT SCAFOLDING REUIRED PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-Disconnect X E-isolation Requester Name : SHYAM TIWARI Phone : 4403 2804
90578649 | 2020-02-24 | A081-1SB220N2 | AC_PIPE RACK 250W LAMP NOT GLOWING-02NOS | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330668 | 700002356603 | ABB MALAYSIA | Electrical | 503.35 | 16 | 192 | end of life | end of life- | Lamps | Replace | 06.02.2020 13:56:50 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. AC_PIPE RACK 250W LAMP NOT GLOWING 02 NOS. NEED TO REPLACE LAMP FOUND NOT GLOWING DURING LIGHTING INSPECTION. 1LFN220N202L314 <(>&<)> 1LFN220N203L109. FPR REF. SEE DRAWING NO. T-4.013.128 SCAFOLDING REQUIRED 2.5MTS FOR BOTH LIGHTS PEFS: Prioriteit: X Scaffold Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : SHYAM TIWARI Phone : 4403 2804 20.02.2020 05:08:46 UTC Mohammad Alam (QRMANR) 7 METER SCAFFOLD REQ, FOR BOTH LAMP
90578650 | 2020-03-12 | A081-1SB220N2 | 1LFN220N208L314 400W LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330667 | 700002356603 | ABB MALAYSIA | Electrical | 75.55 | 8 | 60 | end of life | end of life- | Lamps | Replace | 06.02.2020 13:42:34 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. 1LFN220N208L314 400W LAMP NOT WORKING NEED TO TROUBLESHOOT FOUND NOT GLOWING DURING LIGHTING INSPECTION. FOR REF. SEE DRW NO. T-4.013-400 PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-Disconnect X E-isolation Requester Name : SHYAM TIWARI Phone : 4403 2804
90578651 | 2020-03-12 | A081-1SB220N2 | 1LFN220N208L320 400W LFN NEED TO REPAIR | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330665 | 700002356603 | ABB MALAYSIA | Electrical | 105.92 | 8 | 96 | end of life | end of life- | Lamps | Replace | 06.02.2020 13:27:07 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. Clear description of the problem. 1LFN220N208L320 400W LFN NEED TO REPAIR FOUND NOT GLOWING DURING LIGHTING INSPECTION. SCAFOLDING HEIGHT 11 MTR REQUIRED. DRAWING NO. T-4.013.405 PEFS: Prioriteit: X Scaffold Electrical tasks: X E-Disconnect X E-isolation Requester Name : SHYAM TIWARI Phone : 4403 2804
90578652 | 2020-03-12 | A081-1SB220N2 | 1LFN220N230L111 400W LAMP NEED TO REPAIR | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10330662 | 700002356603 | ABB MALAYSIA | Electrical | 111.84 | 8 | 60 | end of life | end of life- | Lamps | Replace | 06.02.2020 13:15:39 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. 1LFN220N230L111 400WLFN NEED TO REPAIRE FOUND FAULTY DURING LIGHTING INSPECTION. 8 MTS SCAFOLDING REQUIRED PEFS NO T-4.013.404 PEFS: Prioriteit: X Scaffold Electrical tasks: X E-Disconnect X E-isolation Requester Name : Phone :
90578788 | 2020-02-29 | A081-294XA-50200-S | 2ET-LPU-77 EHT TRBLSHOOT&REPLC IF REQ | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10330670 | 700002607282 |  | Instrumentation | 3988.11 | 32 | 136 | Loss of Heating | Loss of Heating-thermostat failed | Heat Tracing | Hardware Replacement | 06.02.2020 14:45:13 UTC Marikkan Thangavel (QRMTH9) Clear description of the problem. 2ET-LPU-77 EHT got alarm two times. Transferred from main to Redundant circuit .Alarms reset. Need to trouble shooting ECM THERMOSTAT. PEFS: Prioriteit: Additional mitigations : Electrical tasks: Requester Name : MARIKKAN Phone : 66853577
90578797 | 2020-02-20 | A081-0S8361A | SDU A INTERNAL INSPECTION RQUIRED | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10330936 | 700001729713 |  | Rotating | 537.27 | 49 | 113 | Preventive Maintenance Work | Preventive Maintenance Work- | Bearing | Check/ Inspect/ Test | 10.02.2020 05:07:58 UTC Raju Sutham (QRRSU3) Clear description of the problem. SDU CENTRIFUGE A BOWL MOTOR FREQURENTLY TRIPPING HIGH TORQUE, AS PER MAINTENNACE INTERNAL INSPECITON RQUIRED, INSTRUMNET , ELECTRICAL AND MECHANGICAL MAINTENANCE SUPPORT REQUIRED FOR INTERNAL INSPECTION PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. CENTRIFUGE NOT AVAILABLE Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-isolation Requester Name : MANOJ Phone : 44032215 26.02.2020 04:17:03 UTC Vincent Mundadan Avarachan (QRVMU1) 70000002
90578858 | 2020-02-18 | A081-0S0143A | 0S-0143A HC FILTER ELEMENT REPLACEMENT | MX04 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10330977 | 700002201324 | DKME | Integrity | 11149.45 | 27 | 46 |  |  |  |  | 10.02.2020 06:52:05 UTC Sunil Kumar Puliyath (QRPSU4) Clear description of the problem. STRING-2 HYDROCARBON FILTER (0S-143A), FILTER CHOCKED AND FILTERELEMENTS NEEDS TO REPLACE. PEFS: T-4.094.330 Prioriteit: Additional mitigations : X JHA needed Requester Name : P SUNIL Phone : 44032115 10.02.2020 11:24:28 UTC Bakthavatchalan Thenral (QRBTH0) ICC template availble
90579762 | 2020-03-18 | A081-1SB220N2 | POOR LIGHTING AC AD PIPE RACK TRAIN -1 | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10331536 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 0 | 0.1 | end of life | end of life- | Lamps | No action | 16.02.2020 20:29:01 UTC Arif Ali Pichimoideen (QRAPI1) Clear description of the problem. AC AD PIPE RACK POOR LIGHTING TO BE CHECK FOLLOWINFG TAGS. 1LFN220N214L320 1LFN220E104L320 1LFN220N224L206 1LFN220N224L211 PEFS: Prioriteit: Additional mitigations : Requester Name : ARIF ALI Phone : 44032313
90580133 | 2020-02-20 | A081-1A8324 | TR1 DAF SCUM BOARD SUPPRT CHAIN CUT FO1 | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10331717 | 700002348718 |  | Integrity | 313.37 | 18 | 18 | Other - please specify in text field | Other - please specify in text field-SCUM BOARD LINKAGE FOUND LOOSEN | Other - please specify in text field | Fix / Repair | 18.02.2020 10:05:50 UTC Eric Ates (QREAT0) Clear description of the problem. TR1 DAF SCUM BOARD CHAIN SUPPORT FOUND CUT/DAMAGED,ONE OUT OF TWO SUPPORT CHAIN WAS CUT/DAMAGED.THIS IS A THREAT TO PRODCUTION IF ONE MORE CHAIN IS CUT IT WILL ENTANGLED WITH THE SCUM TROUGH PLATE. PEFS: T-4.118.867 Prioriteit: Additional mitigations : X Scaffold Requester Name : ERIC ATES Phone : 44032215 20.02.2020 15:05:08 UTC Vudumudi Ravikumar (QRRVU1) SCUM BORAD PULLED UP BY USING MANUAL ROPE, FIX THE DE-LINKED CHAIN AT REQUIRED LOCATION, SCUM BOARD DROPPED DOWN, SHOWN OPERATOR FOUND OK, HOUSE KEEPING PERFORMED.
90580594 | 2020-02-27 | A081-1S0241 | 1S-0241 FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10332055 | 700002354895 | JFC CORPORATION | Integrity | 1883.3 | 60 | 60 |  |  |  |  | 22.02.2020 18:45:29 UTC Sudesh Shetye (QRSSH7) Clear description of the problem. Train-1 1A2 U-0200 lean amine filter 1S-0241 DP on increasing trend, need to be replaced. PEFS: T-13.370.089 Prioriteit: Additional mitigations : X Scaffold X JHA needed Requester Name : GOVIND Phone : 44032111
90580730 | 2020-04-17 | A081-1SB220N2 | AC AREA FAULTY 36w/18w LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10332019 | 700002356603 | ABB MALAYSIA | Electrical | 3355.31 | 60 | 142.8 | end of life | end of life- | Lamps |  | 22.02.2020 06:01:58 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90569669, 90569670)FOUND MANY LAMPS ARE NOT WORKING AND DIFFUSERS DAMAGED AT ALL UNITS ,MAIN PIPERACK, REACTORS SIDE, EXCHANGER SIDE, FIN FAN <(>&<)> FURNISH AREA.SEE ATTACHED DOCUMENT FOR REFERANCE. REQUIRED MATERIALS: 1)36W LAPMS--700 No's) 2)18W LAPMS--240 No's) 3)36W DIFFUSER--20 No's) 4)18W DIFFUSER--15 No's) PEFS: Prioriteit: Additional mitigations : X Scaffold --MOBILE SCAFFOLDING REQUIRED IN BELOW THE MAIN PIPERACK AND REMAINING AREA WILL DO BY 'A' TYPE LADDER. Electrical tasks: X E-Disconnect X E-isolation X JHA needed
90580990 | 2020-03-05 | A081-1SB210N2 | FS-Poor lighting,1R-3025 S-12&FC-10 area | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10332261 | 700002352082 | ABB MALAYSIA | Electrical | 43.02 | 2 | 1 | end of life | end of life- | Lamps | Replace | 26.02.2020 00:02:15 UTC Tarek Elshafei (QRTEL2) Clear description of the problem. Poor Lighting Near 1R-3025 S12 <(>&<)> Recycle gas Valve FC-10 Area. this Rx going to ROR activity. PEFS: Prioriteit: Clear description of the problem, answer the following questions : What actions did you already take to solve the problem, share information. SAP Raised Additional mitigations : X Scaffold Requester Name : tarek Phone : 55341320
90581146 | 2021-01-17 | A081-1SB210N2 | MOC-82772:AB HOT AREA LAMP REPL-LED 18W | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL |  | 700002352082 | ABB MALAYSIA | Electrical | 4257.08 | 0 | 168.1 | Operating at high temperature | Operating at high temperature- | Lamps | Replace
90581164 | 2021-01-13 | A081-1F5111 | HW-1F5111 BNR G4 TIP WELD CORSN;REPL. JC | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10332307 | 700002348459 | KTI | Integrity | 31.48 | 0 | 50 | Material defect | Material defect- | Burner - cup throat | Replace | 26.02.2020 08:59:58 UTC Valerian Rodrigues (QRVRO0) F5111 BURNER G4 TIP FOUND WELDING CORROSION. TIP NEEDS REPLACEMENT.PHOTO ATTACHED 13.01.2021 19:04:29 UTC R. Thridappilly Gopalakrishnan (QRRTH2) REPLACED CRACKED BURNER TIPDURING BURNER CLEANING
90581214 | 2020-04-14 | A081-0S8361A | LEAK,WATER,PIN CENTRIFUGE FEED LINE | MX04 | M_ROT_CENT | Routine Wrk Lvl 1 | 0 |  | CENTRIFUGE | CM | ETP | 10332265 | 700001729713 |  | Rotating | 0 | 36 | 36 |  |  |  |  | 26.02.2020 01:18:33 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. SDU CENTRIFUGE A(0S-8361A) FEED INLET ENTRY PORTION PIN HOLE LEAK PEFS: T-4.253.274 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X JHA needed Requester Name : BASKAR Phone :
90583009 | 2020-03-15 | A081-0P2021 | LEAK WAT ACC CLN PUMP PH 1 | MX04 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10331444 | 700002199414 | PRATISSOLI | Rotating | 67.85 | 11 | 11 |  |  |  |  | 15.02.2020 12:57:13 UTC Mohammad Firdaus bin Abu Bakar (QRMBI2) Clear description of the problem. FO found leak at suction line connection to ACC cleaning pump and discharge line connection to ACC cleaning panel. PEFS: Prioriteit: Additional mitigations : Requester Name : FIRDAUS Phone : 44032213 17.03.2020 15:38:54 UTC Madhan Subramani (QRMSUA) Suction side and discharge side found leak.remove apply tafflon and tighted leak test done no leak job completed.
90584942 | 2020-03-08 | A081-0S0123B | 0S-123 B HC FILTER REPLACEMENT-OPS PRD | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10333054 | 700002200643 | DKME | Integrity | 0 | 0 | 0 |  |  |  |  | 06.03.2020 05:22:27 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123 B FILTER EXHAUSTED, NEED TO BE REPLACED.
90584943 | 2020-03-08 | A081-0S0143B | 0S-143 B HC FILTER REPLACEMENT -OPS PRD | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10333053 | 700002202402 | DKME | Integrity | 0 | 0 | 0 |  |  |  |  | 06.03.2020 05:17:23 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-143 B HC FILTER NEED TO BE REPLACED.
90585065 | 2020-03-28 | A081-294XA-50200-S | 2ET-LDF-029 EHT FAULT;ON REDUNDNT;LFD2 | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10333167 | 700002607282 |  | Instrumentation | 3946.68 | 49 | 151 | Current/voltage -out of limit | Current/voltage -out of limit- | Heat Tracing | Field repair | 08.03.2020 08:55:06 UTC Marikkan Thangavel (QRMTH9) Clear description of the problem. 2ET-LDF-029 frequent EHT alarm observed in Announciation panel and not get reset. Checked field and Transferred to Redundant circuit from main. Reset alarm. At field it found OLD type thermostat need to replace NEW ECM thermostat <(>&<)> RTD. 1.scaffold ,isolation ,insulation removal required. NOTE: Long scaffold required from pipe rack ground floor to pipe line(12m) attached isometric drawing. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: Requester Name : MARIKKAN Phone : 33759904
90586839 | 2020-03-26 | A081-1SB220N2 | 1SB220N2-CKT-12&24 TROUBLESHOOTING | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10333452 | 700002356603 | ABB MALAYSIA | Electrical | 95.52 | 10 | 10 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 11.03.2020 10:50:58 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. During lamps replacement (Ref. WO;90578624 we found that 1SB220N2-circuit -12 and circuit -24 frequently tripping, need to do troubleshooting. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : VASIM Phone : 70567854
90586840 | 2020-07-03 | A081-1SB220N2 | 1SB220N2-2-KA01 C2 CONTACTOR NOT WORKING | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10333450 | 700002356603 | ABB MALAYSIA | Electrical | 2427.35 | 0 | 13 | Loose connection | Loose connection-DAMAGED POWER CONTACTS | Power Contactor | Replace | 11.03.2020 10:43:47 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. During lamps replacement (Ref. WO;90578650 we found that 1SB220N2-2-KA01, C2 contactor L3-line not closing properly. Need to replace. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : VASIM Phone : 70567854 Material Code; 10556709
90587037 | 2020-03-19 | A081-1A8324 | TR1 DAF SCRAPER SMALLER WHEEL D/S OF DE | MX04 | M_X_X | Routine Wrk Lvl 1 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10333679 | 700002348718 |  | Integrity | 82.39 | 86 | 86 | Other - please specify in text field | Other - please specify in text field-WHEELS FOUND DAMEGED | Other - please specify in text field | Replace | 14.03.2020 13:01:43 UTC Leo Miranda (QRLMI0) Clear description of the problem. RI DAF SCRAPER SMALL WHEEL AT THE DOWNSTREAM OF DRIVE END IS OBSERVED IN DAMAGED CONDITION. NEED TO BE RECTIFIED. PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. NO DISTURBANCE YET BUT WILL AFFECT THE DAF PERFORMANCE/ETP OPERATION ONCE BADLY DAMAGED AND UNABLE TO KEEP THE DAF OPERATION. Additional mitigations : Requester Name : LEO Phone : 44032215 19.03.2020 15:50:43 UTC Vudumudi Ravikumar (QRRVU1) DAF BRIDGE WHEELS FOUND BEARING PROBLEM, TWO WHEEL CHANGED WITH NEW WHEELS, HOUSE KEEPING DONE FOUND OK.
90587226 | 2020-03-17 | A081-0P2021 | ASU1 ACC CLEANING PUMP MOTOR VSDS TRIP | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10333871 | 700002199414 | PRATISSOLI | Rotating | 30.45 | 12 | 0 | Other - please specify in text field | Other - please specify in text field-DUE TO HIGH LOAD | Other - please specify in text field | Replace | 16.03.2020 12:30:50 UTC Mohamed Yunus (QRMLI1) Clear description of the problem. ASU 1 ACC CLEANING PUMP MOTOR VSDS TRIP. CHECK AND RECTIFY PEFS: Prioriteit: Additional mitigations : Requester Name : Phone : 17.03.2020 11:51:14 UTC Lakshmanan Shanmughan (QRLSH0) VSDS FAULT ATTENTED , FOUND CLEANING SYSTEM PUMP VSDS INSIDE ONE CONTROL FUSE (5A GLASS TYPE FUSE)BLOWN CONDITION. REPLACED BY NEW ONE. NOW OK.
90587649 | 2020-03-25 | A081-1S0241 | 1S-0241 DP INCREASING,ELEMENT REPLACE | MX04 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10334042 | 700002354895 | JFC CORPORATION | Integrity | 955.01 | 60 | 60 |  |  |  |  | 18.03.2020 10:57:42 UTC Antony Elvin Wilson (QRAWI1) Clear description of the problem. Train-1 1A2 U-0200 lean amine filter 1S-0241 DP on increasing trend, need to be replaced. PEFS: T-13.370.089 Prioriteit: Additional mitigations : X Scaffold X JHA needed Requester Name : Antony Phone : 44032111 19.03.2020 07:19:41 UTC Bakthavatchalan Thenral (QRBTH0) ICC required 5 micron filter is to be used
90587655 | 2020-03-20 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACE OPS PS | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10334110 | 700002201322 | DKME | Integrity | 0 | 46 | 46 |  |  |  |  | 19.03.2020 09:24:30 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. 0S-0123A FILTER ELEMENT TO BE REPLACE PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. CONDENSATE PROCESSING WILL STOP What actions did you already take to solve the problem, share information. S/BY FILTER TAKEN ON LINE Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115 19.03.2020 09:38:21 UTC Bakthavatchalan Thenral (QRBTH0) ICC is live
90588683 | 2020-03-31 | A081-0S0163A | 0S-163 A HC FILTER REPLACEMENT OPS PS | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10334758 | 700002200042 | DKME | Integrity | 0 | 46 | 46 |  |  |  |  | 29.03.2020 06:22:48 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163A HC FILTER IN U-100 STRING-3 NEEDS REPLACEMENT. 29.03.2020 06:30:31 UTC Bakthavatchalan Thenral (QRBTH0) ICC is live now
90589667 | 2020-04-06 | A081-0S0163B | 0S-0163B filter DP high-PRD PS | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10335441 | 700002200043 | DKME | Integrity | 361.24 | 46 | 46 |  |  |  |  | 04.04.2020 22:03:29 UTC Sivakumar Manokaran (QRSMAA) 0S-0163B filter DP high need to repalce the filter element
90589719 | 2020-04-06 | A081-0S0123B | OS 123 B FILTER ELEMENT REPLACEMENT-PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10335470 | 700002200643 | DKME | Integrity | 321.17 | 46 | 46 |  |  |  |  | 05.04.2020 06:31:37 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. OS 123 B FILTER EXHAUSTED AND REPLACE THE FILTER ELEMENT. PEFS: Prioriteit: Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115
90589720 | 2020-04-11 | A081-0P2021 | LEAK WAT ACC CLEANING PUMP DISCH PIPE | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10335473 | 700002199414 | PRATISSOLI | Rotating | 918.73 | 166 | 110 | Other - please specify in text field | Other - please specify in text field-Pin hole leak | Other - please specify in text field | Fix / Repair | 05.04.2020 07:07:43 UTC Bala Subramanian (QRBSU0) Clear description of the problem. ACC CLEANING PUMP DISCHARGE LINE RAISER PIPE WELDING JOINT LEAK TO BE ARRESTED. PEFS: Prioriteit: Additional mitigations : Requester Name : BALASUBRAMANIAN Phone : 44032213 05.04.2020 07:11:29 UTC Jothikumar Manickam (QRJMA1) ASU 3 ACC cleaning unit 20.04.2020 07:31:03 UTC Arunbhai Patel (QRAPA0) Discharge line welding repair done
90589724 | 2020-04-06 | A081-0P2021 | ASU7 ACC CLEANING ASSUMBLY CABLE CONNECT | MX09 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10335475 | 700002199414 | PRATISSOLI | Rotating | 83.04 | 22 | 8 | Other - please specify in text field | Other - please specify in text field-FOR OPR REQUIEST | Other - please specify in text field | Other - please specify in text field | 05.04.2020 07:16:25 UTC Bala Subramanian (QRBSU0) Clear description of the problem. ASU7 ACC CLEANING ASSEMBLY ELECTRICAL CABLE CONNECTION TO BE DONE. PEFS: Prioriteit: Additional mitigations : Requester Name : BALASUBRAMANIAN Phone : 44032213 05.04.2020 07:41:03 UTC Jothikumar Manickam (QRJMA1) cABLE TO BE DISCONNECTED FROM ASU 8 AND TO BE CONNECTED TO ASU 7.
90590087 | 2020-05-03 | A081-0S8361A | SDU-C HVAC B NOT WORKING TO RECTIFY | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10335643 | 700001729713 |  | Rotating | 0 | 30 | 30 | Preventive Maintenance Work | Preventive Maintenance Work-FILTER | Other - please specify in text field |  | 07.04.2020 10:33:43 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. SDU-C HVAC B NOT WORKING TO CHECK AND RECTIFY PEFS: T-4.253.274 Prioriteit: Additional mitigations : Requester Name : CIFAS JEYAKARAN Phone : 44032215 18.05.2020 11:41:27 UTC Sandeep Nair (QRSNAH) Live trouble shooted found SDU-B hvac unit triping due to filter blockage ,cleaned the filter,restaretd the unit, work completed.
90590146 | 2020-06-24 | A081-FIRE HYDRANT | SCE fire hydrant FH84 end cap is seized | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10335710 |  |  |  | 0 | 9 | 9 |  |  |  |  | 08.04.2020 06:41:39 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in March 2020 for UTL S&P, it was found that the end cap at the right-hand side 2.5" outlet at hydrant FH84 was seized. FH84 is located in Road D - 1 opposite Fin Fans. PEFS, location, specification details and pic will be forwarded to OMC. PEFS: Prioriteit: Requester Name : Leo Gaigher
90590236 | 2020-05-16 | A081-0X0104 | DrM FILTER CONVEYOR 0X104 TO BE CLEANED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10335777 | 700002206193 |  | Electrical | 0 | 9 | 12 | Operating outside design | Operating outside design-Logic operating mismatch with celullose | Other - please specify in text field |  | 08.04.2020 23:04:10 UTC Balakrishna Guthu Mijar (QRBMI0) Clear description of the problem. DrM filter conveyer 0X104 to be cleaned after filter batch preparation PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Conveyer may choke and damaged the sight glass What actions did you already take to solve the problem, share information. Before next batch preparation conveyor to be cleaned by mechanical Additional mitigations : Requester Name : Balakrishna.Mijar Phone : 44032115 09.04.2020 04:44:43 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90590251 | 2020-04-12 | A081-2A8324 | TR-2 DAF SMALL WHEEL DAMAGE TO REPLACE | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10335787 | 700002297332 |  | Integrity | 424.03 | 79 | 79 | Other - please specify in text field | Other - please specify in text field-WHEELS FOUND DAMEGED | Other - please specify in text field |  | 09.04.2020 05:22:17 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. TR-2 DAF SCRAPPER SMALL WHEEL NOT ROTATING TO CHECK AND RECTIFY PEFS: T-4.118.867 Prioriteit: Additional mitigations : Requester Name : CIFAS JEYAKARAN Phone : 44032215 09.04.2020 14:57:34 UTC Vudumudi Ravikumar (QRRVU1) DAF PH-2, WHEEL BEARING FOUND DAMGED, WHEELS REPLACED WITH NEW ONE, HOUSE KEEPING DONE. TEST TRAIL DONE IN PRESENCE OF FO, FOUND OK.
90590694 | 2020-04-16 | A081-1A8324 | TR1 DAF FREQUENT TRIPPING | MX04 | E_MOT_LV | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10336062 | 700001736289 | ABB | Electrical | 5745.81 | 112 | 109 | Other - please specify in text field | Other - please specify in text field-WHEELS DRIVE ASSEMBLY FOUND DAMEGED | Other - please specify in text field |  | 13.04.2020 12:47:34 UTC Raja Ganesan (QRRGA0) Clear description of the problem. TR1 DAF1 1AM8324 Frequent trip. Check and rectify. PEFS: T-4.188.864 Prioriteit: Electrical tasks: X E-isolation Requester Name : Raja Ganesan Phone : 44032215 13.04.2020 13:58:04 UTC Joly Poulose (QRJVI4) Carried out trial run and found Motor running current is normal 1.35A and without any warning or trip indication in vsd disply Motor OFF, as per panel it is Torque motion trip, Field instrument and RE for further investigation. 16.05.2020 08:15:37 UTC Vudumudi Ravikumar (QRRVU1) wheel drive assembly replaced with new one, trail run done, found ok.
90590830 | 2020-05-14 | A081-1SB210N2 | MOC-82772:AB HOT AREA LAMP REPL-LED 18W | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL |  | 700002352082 | ABB MALAYSIA | Electrical | 0 | 0 | 0
90591208 | 2020-05-04 | A081-0S0123A | 0S-0123A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10336488 | 700002201322 | DKME | Integrity | 10600.74 | 46 | 46 |  |  |  |  | 19.04.2020 01:25:08 UTC Sivakumar Manokaran (QRSMAA) 0S-0123A filter DP high need to repalce the filter element. 19.04.2020 04:35:57 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90591216 | 2020-04-28 | A081-1S0241 | 1S-0241 FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10336384 | 700002354895 | JFC CORPORATION | Integrity | 1270.2 | 60 | 60 |  |  |  |  | 17.04.2020 11:23:02 UTC Ranganathan Govindarajan (QRRGO9) Train-1 1A2, U-0200 1S-0241 filter DP increased to 1 bar in increasing trend, need to replace filter element. 1A2 Govind 44032111 PEFS : T-13.370.089 19.04.2020 04:45:20 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90591237 | 2021-01-11 | A081-1SB210N2 | AB_FAULTY 400w LAMPS REPALCEMENT (CRANE) | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10336385 | 700002352082 | ABB MALAYSIA | Electrical | 625.97 | 37 | 42 | end of life | end of life- | Lamps |  | 17.04.2020 11:33:55 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. As per ref. WO : 90577896 we replaced 3 no's 400w lamps and remaining 400w lamps- 7no's need to replace in AB compressor house. (Why because 1X-3002 crane safety switch brokered and replacement job hold , due to switch specifications not matching. Once switch ready we will do replacement) Note : Material already withdrawn on this WO; 90577896 PEFS:
90591248 | 2020-04-20 | A081-0S0123A | 0S123 A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10336505 | 700002201322 | DKME | Integrity | 218.5 | 46 | 46 |  |  |  |  | 19.04.2020 06:29:40 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123 A HC FILTER REPLACMENT NEED TO BE DONE.
90591249 | 2020-04-19 | A081-0S0163A | 0S-163 A HC filter replacement | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10336506 | 700002200042 | DKME | Integrity | 293.63 | 46 | 46 |  |  |  |  | 19.04.2020 06:32:44 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163 A HYDROCARBON FILTER NEED TO BE REPLACED.
90591576 | 2020-04-22 | A081-2A8324 | DAF2 SCRAPER SMALL WHEEL NOT ALIGNED | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10336608 | 700002297332 |  | Integrity | 993.62 | 26 | 26 | Other - please specify in text field | Other - please specify in text field-WHEELS FOUND DAMEGED | Other - please specify in text field |  | 20.04.2020 13:10:54 UTC Leo Miranda (QRLMI0) Clear description of the problem. TR-2 DAF SCRAPPER SMALL WHEEL NOT ALIGNED PROPERLY, NOT TOUCH THE RUNWAY SURFACE HENCE NOT ROTATING. ELECTRICAL ISOLATION REQUIRED PEFS: T-4.118.867 Prioriteit: Additional mitigations : Requester Name : LEO Phone : 44032215 23.04.2020 13:02:13 UTC Vudumudi Ravikumar (QRRVU1) ONE WHEEL FOUND NOT ROTATING PROPELRY, THAT WHEEL CHANGED WITH NEW ONE, SHOWN TO OPERATOR FOUND OK.
90591823 | 2020-05-10 | A081-FIRE HYDRANT | ETP fire hydrant FH107 Cam missing | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10336777 |  |  |  | 145.18 | 12 | 12 | Mechanical damage | Mechanical damage- | Other - please specify in text field |  | 22.04.2020 07:38:02 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in April 2020 for UTL Water/ETP, it was found that the Winged Cam Assembly Kit at the right-hand side 2.5" outlet at hydrant FH107 was missing. The spare part MM number is 10687723. FH107 is located in Road E opposite Fire Pumps. PEFS, location, specification details and pic will be forwarded to OMC. PEFS: Prioriteit: Requester Name : Leo Gaigher Phone : 55124684 22.04.2020 10:35:39 UTC Raju Sutham (QRRSU3) MORE DETAILS ARE IN ATTACHED MAIL 15.05.2020 13:47:52 UTC Weston Thampy (QRWTH0) Fire hydrant lock nut replaced with new one
90591845 | 2020-04-24 | A081-0S0163B | 0S-163 B HC FILTER REPLACMENT | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10336888 | 700002200043 | DKME | Integrity | 0 | 0 | 0 |  |  |  |  | 23.04.2020 13:05:02 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163 B HC FILTER REPLACEMENT NEED TO BE DONE. ALREADY FILTER EXHAUSTED , ICC IN LIVE STATE.
90591846 | 2020-04-24 | A081-0S0123A | 0S-123A HC FILTER REPLACEMENT-PRD PS | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10336889 | 700002201322 | DKME | Integrity | 257.02 | 0 | 0 |  |  |  |  | 23.04.2020 13:07:15 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123 A HC FILTER REPLACEMENT REQUIRED ONCE THE FILTER GETS EXHAUSTED, CURRENTLY THE DP IS APPROACHING TO THE ALARM VALUE.
90592028 | 2020-10-11 | A081-0A8350 | BSTD BAY8 ZONE B ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10336851 | 700002779390 |  |  | 4121.65 | 378 | 378 | Material defect | Material defect- | Other - please specify in text field | Replace | 23.04.2020 08:28:34 UTC Vaghasiya Bhimjibhar (QRVBH2) Clear description of the problem. BROKEN GLASS TO BE REPLACED IN BAY - 8, ZONE-B, LONG GLASS QTY. 1 NO. PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. SLUDGE CANNOT BE LOADED IF THE ROOF GLASS IS BROKEN Additional mitigations : X Use moveable platform or man lift X Scaffold X Crane CRANE NEEDED TO LIFT THE ROOF CART TO THE TOP Electrical tasks: X E-isolation X JHA needed Requester Name : SAI Phone : 74091660 15.08.2020 12:52:06 UTC Praveen Gowda (QRPGO8)
90592857 | 2020-05-20 | A081-1F5111 | 1F5111 WINDOW FLAPR BNR-G&F;REPLC** | MX04 | M_FUR_X | Routine Wrk Lvl 2 | 0 |  | SMR FURNACE | CM | LPU | 10337695 | 700002348459 | KTI | Integrity | 0 | 98 | 53 | Fouling | Fouling-Insulation may be fouled | Other - please specify in text field |  | 02.05.2020 23:24:44 UTC Ferdinand Balinos (QRFBA2) Clear description of the problem. 1F-5111 observation window flapper damaged (melted) on upper window G eastside (on G15 side). PEFS: Prioriteit: Requester Name : Ferdinand Balinos Phone : 66480081 21.05.2020 13:49:33 UTC Velmurugan Subramanian (QRVSU0) Both F ang G floppers replaced by new ones. In F ,all locking bolts provided along with spring lock, it is working good. In G , The flopper locking screws sheared during removal .Spring lock bolt also sheared. New window flopper provided. Spring lock bolt need to be extracted during TA , currently the spring is locked with nearby frame bolt. 80 percent of spring action is available.
90592879 | 2020-05-28 | A081-2SB210N2 | 2R-3011A/B 2ND FLR ALL FLOOD LIGHT FAULT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10337593 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 12 | 12 | Internal failure / short | Internal failure / short- | Lighting Fixture |  | 01.05.2020 12:50:58 UTC Chon Sung Ong (QRCON0) Clear description of the problem. 2R-3011/12 A/B. Second floor (Inlet valve platform) All Flood light not working. PEFS: Prioriteit: Additional mitigations : X Scaffold Requester Name : Ong Chon Sung Phone : 44032311 28.05.2020 12:35:31 UTC Sudheer Kumar Pendurthi (QRSPE6) Found 2SB210N2-CKT-19 tripped , due to 2LFN210N219L306 lamp faulty. Lamp supply dis-connected from JB (2JB7719076) then reseted OK now and for troubleshooting we raised separate notification( Ref NT No-10339643) .
90592896 | 2020-05-04 | A081-0S0163A | 0S-0163A filter choke -OPS PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10337650 | 700002200042 | DKME | Integrity | 0 | 46 | 46 |  |  |  |  | 02.05.2020 10:06:27 UTC Sivakumar Manokaran (QRSMAA) 0S-0163A filter choke need to clean the filter element
90592897 | 2020-05-04 | A081-0S0123A | 0S-0123A fitler DP high -PRD PS | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10337651 | 700002201322 | DKME | Integrity | 0 | 46 | 46 |  |  |  |  | 02.05.2020 10:08:57 UTC Sivakumar Manokaran (QRSMAA) 0S-0123A filter DP high need tor epalce the fitler element
90593048 | 2020-10-30 | A081-0A8350 | BSTD BAY1 ZONE A ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10337735 | 700002779390 |  |  | 2746.49 | 225 | 239 | Other - please specify in text field | Other - please specify in text field-GLASS BROKEN | Other - please specify in text field | Replace | 03.05.2020 11:31:49 UTC Eric Ates (QREAT0) Clear description of the problem. BROKEN GLASS (1PC) TO BE REPLACE IN BAY1 ZONE A (SMALL GLASS.NOTE: 0T8361 USED FOR SAP PURPOSES ONLY. PEFS: Prioriteit: Additional mitigations : Requester Name : SAI Phone : 74091660 15.08.2020 12:52:25 UTC Praveen Gowda (QRPGO8) planner remarks : Please Take Care While Preparing permit IDENFITY GLASS LOCA AS PER DRA / BAY NO BROKENGLASS SIZE:1880X484MM(SMALL GLASS) NEW GLASS AVABILE BEHIND CURNING BAY 27.10.2020 23:15:26 UTC Arunbhai Patel (QRAPA0) Total of 19 no of Roof Glasses Replaced in WO no 90593048/90609920/90610624/90610217
90593049 | 2020-10-25 | A081-0A8350 | BSTD BAY7 ZONE A ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10337737 | 700002779390 |  |  | 2753 | 478 | 302 | Material defect | Material defect- | Other - please specify in text field | Replace | 03.05.2020 11:36:59 UTC Eric Ates (QREAT0) Clear description of the problem. BROKEN GLASS (1PC) TO BE REPLACE IN BAY7 ZONE A (SMALL GLASS.NOTE: 0T8361 USED FOR SAP PURPOSES ONLY. PEFS: Prioriteit: Additional mitigations : Requester Name : SAI Phone : 74091660 13.05.2020 09:44:00 UTC Praveen Gowda (QRPGO8) LATEST UDPATE FROM FO :BROKEN GLASS (2PC) TO BE REPLACE IN BAY7 ZONE A (SMALL GLASS.NOTE: 0T8361 USED FOR SAP PURPOSES ONLY. 15.08.2020 12:56:48 UTC Praveen Gowda (QRPGO8) planner remarks : Please Take Care While Preparing permit IDENFITY GLASS LOCA AS PER DRA / BAY NO BROKENGLASS SIZE :1880X484MM(BIG GLASS): 2 GLASS BROKEN NEW GLASS AVABILE BEHIND CURNING BAY 15.08.2020 12:59:46 UTC Praveen Gowda (QRPGO8) LATEST UDPATE ON AUGUST 15TH 2020 planner remarks : Please Take Care While Preparing permit IDENFITY GLASS LOCA AS PER DRA / BAY NO BROKENGLASS SIZE :1880X484MM( SMALL GLASS) 2 QTY
90593050 | 2020-10-13 | A081-0A8350 | BSTD BAY6 ZONE A ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10337738 | 700002779390 |  |  | 3055.07 | 315 | 322 | Other - please specify in text field | Other - please specify in text field-one glass broken | Other - please specify in text field | Replace | 03.05.2020 11:39:13 UTC Eric Ates (QREAT0) Clear description of the problem. BROKEN GLASS (1PC) TO BE REPLACE IN BAY6 ZONE A (SMALL GLASS.NOTE: 0T8361 USED FOR SAP PURPOSES ONLY. PEFS: Prioriteit: Additional mitigations : Requester Name : SAI Phone : 74091660 15.08.2020 12:58:14 UTC Praveen Gowda (QRPGO8) planner remarks : Please Take Care While Preparing permit IDENFITY GLASS LOCA AS PER DRA / BAY NO BROKENGLASS SIZE :1880X484MM(SMALL GLASS) 1QTY NEW GLASS AVABILE BEHIND CURNING BAY 09.10.2020 09:22:59 UTC Arunbhai Patel (QRAPA0) one glass new glass replaced
90593695 | 2020-06-21 | A081-1SB220N2 | AC AREA FAULTY 36w/18w LAMPS REPLACEMENT | MX04 | E_SWB_D | UserDefined Priority | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10337498 | 700002356603 | ABB MALAYSIA | Electrical | 5929.22 | 98 | 410 | end of life | end of life- | Lamps |  | 30.04.2020 10:07:29 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. ON REF. WO:90580730 WE ARE ALREADY REPLACED 162 NO'S 18w LAMPS REMAINING LAMPS <(>&<)> DIFFUSERS NEED TO REPLACE AT ALL UNITS ,MAIN PIPERACK, REACTORS SIDE, EXCHANGER SIDE, FIN FAN <(>&<)> FURNISH AREA.SEE ATTACHED DOCUMENT FOR REFERANCE. REQUIRED MATERIALS: 1)36W LAPMS--700 No's 2)36W DIFFUSER--20 No's 3)18W DIFFUSER--15 No's 4)18W LAMPS--80 No's (18w lamp MM 10546223 in hand , material withdrawn from wo 90577889) PEFS: Prioriteit:
90594063 | 2020-05-20 | A081-2SB210N2 | 2R-3025 Fluorescent Light not working | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10338450 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 10.1 | 10.1 | end of life | end of life- | Lamps |  | 11.05.2020 19:28:38 UTC Chon Sung Ong (QRCON0) Clear description of the problem. 2R-3025 Fluorescent Light Not Working As per below List 1. 2LFE210E104L107 (S04 Location) 2. 2LFN210N221L203 (S04 Location) 3. 2LFN210N215L302 (S11 Location) 4. 2LFN210N221L222 (S11 Location) 5. 2LFN210N221L310 (S03 Location) 6. 2LFN210N215L210 (S12 Location) This light Require for incoming CCO Activity PEFS: Prioriteit: Additional mitigations : X Scaffold Requester Name : Ong Chon Sung Phone : 44032311 12.05.2020 06:35:09 UTC Mohammad Alam (QRMANR) 36<(>&<)> 18W lamp in hand but withdraw through other Wo 90570778 , base on Operation priority we used this material in 2R3025 CCO reactor.
90594084 | 2020-05-25 | A081-1A8324 | DAF-2 Scraper Small Wheel Damaged | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10338437 | 700002348718 |  | Integrity | 0 | 22 | 22 | Normal Wear | Normal Wear- | Valve body |  | 11.05.2020 12:43:07 UTC Ron Sorreno (QRRSO1) Clear description of the problem. Train 2 DAF Flotation Scarper Small Wheel Bearing DAMAGE abnormal sound observed. Being witnessed by our maintenance guys Ferdie. PEFS: T-4.118.864 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X Scaffold Electrical tasks: X JHA needed Requester Name : Ron Sorreno Phone : 44032215 15.05.2020 14:14:46 UTC Weston Thampy (QRWTH0) 2A-8324 Small wheel replaced with new ,Total 2 nos.
90594165 | 2021-01-07 | A081-0A8350 | BSTD BAY3 ZONE B ROOF GLASS CHANGE | MX04 | M_X_X | Routine Wrk Lvl 2 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10338501 | 700002779390 |  | Integrity | 9341.27 | 286 | 286 | Mechanical damage | Mechanical damage- | Other - please specify in text field | Replace | 12.05.2020 10:43:00 UTC Ebrayeem Gnanakkon (QREGN1) Clear description of the problem. BSTD Bay-3 Zone B Roof glass broken is to replace PEFS: Prioriteit: Additional mitigations : X Use moveable platform or man lift
90594523 | 2020-05-25 | A081-2SB210N2 | BB AREA LIGHT FIXTURES DIFFUSER DAMAGED | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10338738 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 6 | 6 | Mechanical damage | Mechanical damage- | Lighting Fixture |  | 15.05.2020 06:52:57 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. Found in BB area some locations 2 x 36W fluorescent fixtures diffusers damaged Observed by FO. Need to be replace ASAP.Due to Ex integrity gone For your reference see attached mail. No need scaffolding. We will do by ladder. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : SUDHEER Phone : 70483198 19.05.2020 08:31:38 UTC Mohammad Alam (QRMANR) CURRENTLY 4 NUMBER DIFFUSER AVAILABLE IN STOCK.
90594586 | 2020-05-18 | A081-1S0241 | 1S-0241 filter element to be rplaced. | MX09 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10338851 | 700002354895 | JFC CORPORATION | Integrity | 958.09 | 60 | 60 |  |  |  |  | 17.05.2020 10:07:49 UTC Murahari Korlam (QRMKO0) 1S-0241 filter DP increased to 1.2 bar,in increasing trend, need to replace filter element. Murahari 44032111 PEFS : T-13.370.089
90594679 | 2020-06-01 | A081-0S0123B | 0S-0123B HC FILTER REPLACEMENT | MX04 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10338903 | 700002200643 | DKME | Integrity | 0 | 0 | 47 |  |  |  |  | 18.05.2020 04:13:20 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123B HC FILTER REPLACEMENT NEED TO BE DONE. 18.05.2020 07:49:51 UTC Bakthavatchalan Thenral (QRBTH0) new notification is raised with different priority.Also this WO is approved in MX-04 hence this notification and WO are cancelled
90594682 | 2020-05-20 | A081-0S0163B | 0S-0163B HC FILTER REPLACMENT ops PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10338904 | 700002200043 | DKME | Integrity | 28554.86 | 47 | 47 |  |  |  |  | 18.05.2020 04:18:14 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163B HC FILTER REPLACEMENT NEED TO BE DONE IN U-100 STRING-3
90594722 | 2020-05-18 | A081-0S0123B | 0S123B HC FILTER REPLACEMENT OPS PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10338916 | 700002200643 | DKME | Integrity | 0 | 47 | 47 |  |  |  |  | 18.05.2020 08:59:51 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123B HC FILTER NEED TO BE REPLACED.
90594854 | 2020-05-20 | A081-0P2021 | ASU-3 ACC CLEANING PUMP ELECTRICAL PROBL | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10338976 | 700002199414 | PRATISSOLI | Rotating | 344.3 | 24 | 0 | Other - please specify in text field | Other - please specify in text field-WATER INGRESS IN THE SWITCH | Other - please specify in text field |  | 19.05.2020 01:19:23 UTC Puran Kabadwal (QRPKA4) Clear description of the problem. ASU-3 ACC cleaning pump can not start due to on local panel showing emergency stop active. PEFS: Prioriteit: Additional mitigations : Requester Name : PURAN Phone :
90595295 | 2020-06-10 | A081-2SB210N2 | GUARD BED AREA POOR LIGHTING | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10339276 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 0 | 4 | Internal failure / short | Internal failure / short-2SB210N2-CKT-19 TRIPPED | Lamps | Adjust / reset | 22.05.2020 01:18:04 UTC Faizan Ahemed Ali Sharfudeen (QRFSH3) Clear description of the problem. 2R-3011/12 GUARD BED AREA POOR LIGHTING BECAUSE OF LIGHTS NOT BLINKING IN 1ST AND 2ND ELEVATION. PEFS: NA Prioriteit: Additional mitigations : Requester Name : FAIZAN AHEMED ALI Phone : 4403-2311 28.05.2020 12:34:35 UTC Sudheer Kumar Pendurthi (QRSPE6) Found 2SB210N2-CKT-19 tripped , due to 2LFN210N219L306 lamp faulty. Lamp
90595727 | 2020-10-08 | A081-0A8350 | BSTD BAY9 ZONE A ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 2 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10339553 | 700002779390 |  |  | 0 | 262 | 284 | Other - please specify in text field | Other - please specify in text field-3 no glass broken | Other - please specify in text field | Replace | 27.05.2020 11:26:44 UTC Ebrayeem Gnanakkon (QREGN1) Clear description of the problem. BROKEN GLASS TO BE REPLACE IN BAY9 ZONE A (SMALL GLASS) PEFS: Prioriteit: X Use moveable platform or man lift X Crane FOR ROOF CART LIFTING. X JHA needed Requester Name : Ebrayeem Phone : 44032215 15.08.2020 13:05:18 UTC Praveen Gowda (QRPGO8) planner remarks : Please Take Care While Preparing permit IDENFITY GLASS LOCA AS PER DRA / BAY NO BROKENGLASS SIZE :1880X484MM( SMALL GLASS)1 QTY NEW GLASS AVABILE BEHIND CURNING BAY 09.10.2020 09:26:15 UTC Arunbhai Patel (QRAPA0) 3 new glass replaced
90595749 | 2020-06-11 | A081-0S0143A | 0S-143A DP high | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10339622 | 700002201324 | DKME | Integrity | 480.85 | 47 | 47 |  |  |  |  | 28.05.2020 10:04:11 UTC Elangovan Muthusamy (QREMU0) 0S-143A DP high filter element to be replaced
90595750 | 2020-06-26 | A081-0S0123B | 0S-123B DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10339621 | 700002200643 | DKME | Integrity | 0 | 47 | 47 |  |  |  |  | 28.05.2020 10:02:37 UTC Elangovan Muthusamy (QREMU0) 0S-123B DP high filter element to be replaced.
90596004 | 2020-06-01 | A081-0P2021 | FS ACC CLEANING CABLE CONNECTION ASU 3 | MX09 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10338974 | 700002199414 | PRATISSOLI | Rotating | 0 | 24 | 8 | Other - please specify in text field | Other - please specify in text field-HIGH TEMPORATURE | Other - please specify in text field | Replace | 19.05.2020 01:10:32 UTC Puran Kabadwal (QRPKA4) Clear description of the problem. ASU-1 ACC top ,for ACC cleaning ,electrical cables are damaged & cracked. Need to be replaced. ACC cleaning suspend till cable replacement. May cause electric shock. PEFS: Prioriteit: Additional mitigations : Requester Name : PURAN Phone : 31.05.2020 11:56:11 UTC Jothikumar Manickam (QRJMA1) acc CLEANING CABLE CONNECTION REQUIRED IN asu 3
90598606 | 2020-07-11 | A081-0S0123B | 0S-0123B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10340552 | 700002200643 | DKME | Integrity | 0 | 47 | 47 |  |  |  |  | 02.06.2020 12:35:36 UTC Sivakumar Manokaran (QRSMAA) 0S-0123B filter DP high need to repalce the filter element.
90598749 | 2020-07-09 | A081-1SB220N2 | POOR LIGHTING IN T1 LDS AREA AD PIPERACK | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10340706 | 700002356603 | ABB MALAYSIA | Electrical | 820.79 | 30 | 88 | end of life | end of life- | Lamps |  | 04.06.2020 00:38:04 UTC Allan Maligalig (QRAMA9) Clear description of the problem. T1 LETDOWN STATION AREA IN AD PIPE RACK IS HAVING POOR LIGHTING, MAJORITY OF THE POST LAMP ARE NOT LIT, NEED TO CHECK AND REPLACE LIGHT TUBES/LAMP. STEP LADDER REQUIRED. PEFS: Prioriteit: Additional mitigations : Electrical tasks: Requester Name : ALLAN MALIGALIG Phone : 44032218 13.06.2020 07:46:33 UTC Prabakaran Subramanian (QRPSU8) Phone 70482061 FLOC CHANGED FROM A081-0J6003A/ MPS/LPS DESUPERHEATER TO LIGHTING SWITCH BOARD A081-1SB220N2/ 700002356603.
90598830 | 2020-10-11 | A081-0A8350 | BSTD BAY8 ZONE B ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10340896 | 700002779390 |  |  | 0 | 232 | 254 | Material defect | Material defect- | Other - please specify in text field |  | 07.06.2020 07:34:24 UTC Ebrayeem Gnanakkon (QREGN1) Clear description of the problem. Replace BSTD Bay-8 Zone B one small roof glass. PEFS: Prioriteit: X WPS/ Work instruction needed X Use moveable platform or man lift X Crane For Roof cart lifting. X JHA needed Requester Name : Ebrayeem Phone : 44032215 15.08.2020 13:06:22 UTC Praveen Gowda (QRPGO8) planner remarks : Please Take Care While Preparing permit IDENFITY GLASS LOCA AS PER DRA / BAY NO BROKENGLASS SIZE :1880X484MM( SMALL GLASS) 1QTY NEW GLASS AVABILE BEHIND CURNING BAY 15.10.2020 01:39:58 UTC Yogarajan Pandiyan (QRYPA0) All the Broken roof glasses replaced in Both zones.
90599781 | 2021-03-28 | A081-0S0163A | 0S-0163A HC FILTER REPLACEMENT-> | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10341599 | 700002200042 | DKME | Integrity | 12513.57 | 27 | 47 |  |  |  |  | 17.06.2020 13:42:30 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163 A HC FILTER NEED TO BE REPLACED ONCE IT GETS EXHAUSTED.
90600464 | 2020-11-01 | A081-2SB210N2 | Non Glowing Lights Poor Illumination | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10341669 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 8 | 8.1 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 19.06.2020 00:48:56 UTC Rajeshkannan Barathkumar (QRRBAL) Clear description of the problem. POOR ILLUMINATION FOLLOWING LIGHTS NEED TO ATTEND. 2R-3024 REACTOR TOP NORTH SIDE TWO LIGHTS. 2R-3025 REACTOR TOP NORTH SIDE ONE LIGHT. 2R-3026 REACTOR TOP NORTH SIDE ONE LIGHT. 2R-3029 REACTOR TOP NORTH SIDE ONE LIGHT. SCAFFOLDING REQUIRED. PEFS:
90600518 | 2021-04-10 | A081-0S0163A | 0S-0163A DP HIGH-> | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10341813 | 700002200042 | DKME | Integrity | 275.48 | 27 | 47
90600944 | 2020-07-09 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10342030 | 700002200043 | DKME | Integrity | 476.6 | 47 | 47 |  |  |  |  | 25.06.2020 06:42:51 UTC Elangovan Muthusamy (QREMU0) 0S-163B DP high filter element to be replaced.
90600945 | 2020-06-30 | A081-0S0123A | 0S-0123A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10342027 | 700002201322 | DKME | Integrity | 0 | 47 | 47 |  |  |  |  | 25.06.2020 06:37:37 UTC Elangovan Muthusamy (QREMU0) 0S-123A DP high filter element to be replaced.
90600946 | 2021-01-09 | A081-0S0143A | 0S-0143A DP HIGH-> | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10342028 | 700002201324 | DKME | Integrity | 610.08 | 27 | 47 |  |  |  |  | 25.06.2020 06:39:10 UTC Elangovan Muthusamy (QREMU0) 0S-143A DP high filter element to be replaced
90600947 | 2020-08-29 | A081-0S0143B | 0S-0143B DP HIGH-> | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10342029 | 700002202402 | DKME | Integrity | 0 | 47 | 47 |  |  |  |  | 25.06.2020 06:40:50 UTC Elangovan Muthusamy (QREMU0) 0S-143b DP high filter element to be replaced.
90602028 | 2020-07-11 | A081-0X0104 | 0X-0104 screw conveyor to be cleaned | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10342996 | 700002206193 |  | Electrical | 0 | 6 | 12 | Fouling | Fouling-moisture deposit | drive system | Cleaned | 06.07.2020 00:57:54 UTC Elangovan Muthusamy (QREMU0) DrM filter 0X-104 screw conveyor to be cleaned for next batch preparation. 06.07.2020 04:35:10 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90602348 | 2020-07-22 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10343190 | 700002201322 | DKME | Integrity | 0 | 47 | 47 |  |  |  |  | 08.07.2020 06:26:22 UTC Balakrishna Guthu Mijar (QRBMI0) string-1 condensate filter element 0S-0123A to be replace.
90602618 | 2020-07-13 | A081-0S0123B | 0S123B HC FILTER REPLACEMENT-PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10343408 | 700002200643 | DKME | Integrity | 0 | 47 | 47 |  |  |  |  | 12.07.2020 03:55:41 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S123B HC FILTER REPLACEMENT NEED TO BE DONE.
90602729 | 2020-07-14 | A081-0S0163A | 0S-163A DP HIGH-PRD PS | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10343449 | 700002200042 | DKME | Integrity | 0 | 47 | 47 |  |  |  |  | 13.07.2020 02:19:25 UTC Elangovan Muthusamy (QREMU0) 0S-163A DP High filter element to be replaced.
90603040 | 2020-07-25 | A081-2A8324 | FS-TR2 DAF SCRAPPER 2A-8324 VSD ALARM | MX04 | E_MOT_LV | Routine Wrk Lvl 2 | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10344391 | 700002297890 | ABB | Electrical | 0 | 8 | 8 | Overload | Overload- | Protection Relay / MCU | Check/ Inspect/ Test | 15.07.2020 00:49:38 UTC Eric Ates (QREAT0) Clear description of the problem. TR2 DAF SCRAPPER 2A-8324 VSD ALARM OBSERVED.NEED TO CHECK AND RECTIFY. PEFS: T-4.1118.867 Prioriteit: Additional mitigations : Requester Name : ERIC ATES Phone : 44032215 Enter text here... 26.07.2020 01:23:43 UTC Mutharasu Subbaih (QRMSU8) Checked and found Motor Temperature Warning alarm is persisting, Checked motor rating 1.5Kw and Full Load Currrent-1.9Amps start up data, fault function parameters are found ok.Runing Parameters checked in the VSDS display Current- fluctuating 1.98 to 1.66amps some times current going up to 2.1apms.Torque fluctuating from 16% to 35%, It seems that motor getting over loaded, So mechanical need to be checked. 26.07.2020 01:53:52 UTC Mutharasu Subbaih (QRMSU8) Motor Temperature Estimated -98.1degree C, RPM-1110 28.07.2020 05:13:06 UTC Prabakaran Subramanian (QRPSU8) Phone 70482061 REFER ATTACHED RE RECOMMENDATION MAIL FOR REFERENCE, AS PER OMC CONFIRMATION AND NEW NOTIFICATION TO MUMZC- 10345410 ALREADY CREATED HENCE THIS WO CAN BE CLOSED.
90603195 | 2020-08-04 | A081-0X0104 | 0X-0104 DrM FILTER CONVEYOR TO BE CLEANE | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10344562 | 700002206193 |  | Electrical | 0 | 9 | 12 | Coking | Coking- | drive system | Cleaned | 17.07.2020 01:27:36 UTC Balakrishna Guthu Mijar (QRBMI0) 0X-0104 DrM FILTER CONVEYOR TO BE CLEANED AFTER BATCH PREPARATION 19.07.2020 06:17:40 UTC Bakthavatchalan Thenral (QRBTH0) ICC Required
90603205 | 2020-08-10 | A081-1S0241 | 1S-0241 FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10344528 | 700002354895 | JFC CORPORATION | Integrity | 955.36 | 60 | 60 |  |  |  |  | 16.07.2020 10:22:13 UTC Murahari Korlam (QRMKO0) 1S-0241 filter DP increased to 1.2 bar,in increasing trend, need to replace filter element. After backwashing, there isn't much improvement. Murahari 44032111 PEFS : T-13.370.089 19.07.2020 06:34:36 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90603263 | 2020-12-08 | A081-2SB210N2 | 2SB210N2-Q52 -LIGHTING NEED TO CHECK | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10344731 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 0 | 62 | Internal failure / short | Internal failure / short- | Power Supply | Repair / correct
90603936 | 2020-07-25 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10345133 | 700002200043 | DKME | Integrity | 29088.71 | 47 | 47 |  |  |  |  | 23.07.2020 20:34:36 UTC Balakrishna Guthu Mijar (QRBMI0) 0S-0163B filter element replacement
90604178 | 2021-02-27 | A081-2A8324 | TR2 SCRAPER WHEELS REPLACEMENT/REPAIR | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10345410 | 700002297332 |  | Rotating | 1201.66 | 56 | 56
90604572 | 2020-08-01 | A081-2A8324 | TR2 DAF SCRAPER NDE SMALL WHEEL DAMAGED | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10345648 | 700002297332 |  | Integrity | 0 | 0 | 0 | Normal Wear | Normal Wear-small wheel damaged | Rotating element | Replace | 30.07.2020 18:30:32 UTC Leo Miranda (QRLMI0) Clear description of the problem. TRAIN 2 DAF SCRAPER NDE SMALL WHEEL IS FOUND DAMAGED CONDITION. NEED TO BE ATTENDED AT THE EARLIEST BEFORE GOT WORSE. PEFS: Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. BRIDGE WILL FREQUENTLY TRIP ON HIGH TORQUE IF THE WHEEL IS NOT RUNNING SMOOTH. HENCE WILL RESULT IN POOR SCUM REMOVAL IN THE FLOTATOR. Additional mitigations : Electrical tasks: X E-isolation Requester Name : LEO Phone : 44032215 02.08.2020 20:11:32 UTC Rakeshkumar Mansukhbhai Rathod (QRRRA1) NDE small damaged wheel replaced with newone. Job completed. abc
90604915 | 2020-08-12 | A081-1A8324 | DAF-1 SCRAPPER SMALL WHEEL DAMAGED | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10345849 | 700002348718 |  | Integrity | 383.72 | 86 | 86 | Normal Wear | Normal Wear-SCRAPPER SMALL WHEEL DAMAGED | Other - please specify in text field | Fix / Repair | 03.08.2020 13:11:11 UTC Vaghasiya Bhimjibhar (QRVBH2) Clear description of the problem. 1A:8324 small wheel down stream of drive end first wheel outside is wobbling. Scaffolding already available. PEFS: Prioriteit: Additional mitigations : X WPS/ Work instruction needed X Scaffold Requester Name : Rajesh vaghasiya Phone : 44032215 15.08.2020 19:44:28 UTC Weston Thampy (QRWTH0) Ensured ICC is live. 2. Ensured erection of access scaffolding with green tag and valid inspection date. 3. Lifted the bridge by using hydraulic jack and put the wooden planks packing below the bridge. 4. Released the hydraulic jack and remove it from the bottom of the bridge. 5. Removed the damaged small wheel. 6. Fixed new small wheel in place. 7. Lifted the bridge by using hydraulic jack and remove the wooden planks from downside of the bridge.
90604918 | 2021-07-28 | A081-0A8350 | BAY7&8BSTD ZONE B WALLGLASS BRO(1QTY)OK | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10345619 | 700002779390 |  | Integrity | 4184.39 | 169 | 169
90605615 | 2020-08-10 | A081-0A8350 | BSTD FREQUENT TRIPPING TO BE RECTIFIED | MX04 | M_X | Schedule Breaker | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10345638 | 700002779390 |  |  | 0 | 10 | 8 | Loose connection | Loose connection- | Cable / Terminations | Adjust / align | 30.07.2020 13:02:44 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. BSTD FREQUENT TRIPPING ,NEED SUPPORT FROM ELECTRICAL AND INSTRUMENT DEPARTMENT TO RECTIFY THE ISSUE PEFS: Prioriteit: Additional mitigations : X WPS/ Work instruction needed Requester Name : RAJA RAMASAMY Phone : 44032215 17.08.2020 22:15:07 UTC Siby George (QRSGE0) No reason found. The system got reset. The relay 7K10 was found released
90605838 | 2021-04-20 | A081-1F5111 | 1F5111 WINDOW G GAP,INSP,RECTIFY;WNTR | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10345737 | 700002348459 | KTI | Integrity | 0 | 0 | 12
90605938 | 2022-03-19 | A081-0A8350 | BAY2&3 BSTD ZONE B WALL GLASS BROK(5QTY) | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10346501 | 700002779390 |  | Integrity | 7338.64 | 288.3 | 288.3
90606046 | 2020-10-17 | A081-0A8350 | BSTD BAY7 ZONE B ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10346318 | 700002779390 |  |  | 0 | 551 | 242 | Material defect | Material defect- | Other - please specify in text field | Replace | 10.08.2020 10:56:47 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. BSTD BAY 7 , ZONE B ,5 NOS OF SMALL GLASS BROKEN TO BE RECTIFIED PEFS: Prioriteit: Additional mitigations : Requester Name : RAJA RAMASAMY Phone : 44032215 12.08.2020 06:05:52 UTC Raju Sutham (QRRSU3) BSTD BAY 7,ZONE B ,5 ROOF SMALL GLASS BROKEN CONDITION, NEED TO FIX. 18.08.2020 12:04:53 UTC Praveen Gowda (QRPGO8) IDENFITY GLASS LOCA AS PER DRA / BAY NO BROKENGLASS SIZE :1880X484MM(SMALL GLASS) 5 QTY NEW GLASS AVABILE BEHIND CURNING BAY 26.10.2020 01:07:37 UTC Yogarajan Pandiyan (QRYPA0) Total of 25 no of Roof glasses replaced in the WOs90609944, 90593049, 90606046
90606226 | 2020-10-25 | A081-1SB210N2 | AB_1R-3026 AREA 36/18W LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10346764 | 700002352082 | ABB MALAYSIA | Electrical | 0 | 8 | 8 | end of life | end of life- | Lamps | Replace | 15.08.2020 20:22:13 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING LIGHTING INSPECTION REF.WO; 90605198 OBSERVED 36W--10 No's <(>&<)> 18w--8 No's LAMPS NOT WORKING NEAR 1R-3026. NEED TO REPLACE FAULTY LAMPS Note: Priority for 1R-3026 CCO activities. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X JHA needed Requester Name : SUDHEER Phone : 70483198 MATERIAL IN HAND
90606235 | 2020-09-01 | A081-1SB210N2 | PMFLT-1SB210N2-Q52-LIGHTING CKT TO CHECK | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10346762 | 700002352082 | ABB MALAYSIA | Electrical | 248.56 | 12 | 10.1 | Internal failure / short | Internal failure / short- | Lighting Fixture |  | 15.08.2020 20:12:32 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING LIGHTING INSPECTION REF.WO; 90605198 OBSERVED IN 1SS210, 1SB210N2-Q52 (CIRCUIT 41) LIGHTING CIRCUIT TRIPPED CONDITION.WE TRIED TO RESET BUT NOT EABLE TOR ESET. NEED TO DO TROUBLESHOOT. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : SUDHEER Phone : 70483198
90607255 | 2020-12-13 | A081-0S0143B | 0S-0143B FILTER DP HIGH-> | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10347581 | 700002202402 | DKME | Integrity | 0 | 27 | 47
90607524 | 2020-10-23 | A081-0A8350 | BSTD BAY5 ZONE B ROOF SMALL GLASS BROK | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10347711 | 700002779390 |  |  | 0 | 520 | 290 |  | -Roof Glasses broken | Other - please specify in text field | Replace | 26.08.2020 01:40:44 UTC Nimish Patel (QRNPA4) BSTD BAY 05 Zone A 03 roof glass and one small side glass broken Scaffolding required to attend this glass broken job Ensure BAy should be empty 27.08.2020 04:51:30 UTC Raju Sutham (QRRSU3) Clear description of the problem. BSTD BAY 05 Zone A 03 roof glass and one small side glass broken Scaffolding required to attend this glass broken job Ensure BAy should be empty PEFS: Prioriteit: Additional mitigations : X Use moveable platform or man lift Requester Name : NIMESH Phone : 55276258 01.09.2020 08:35:43 UTC Raju Sutham (QRRSU3) this notification only for roof glass, wall glass new notification will create. 02.09.2020 08:24:51 UTC Praveen Gowda (QRPGO8) IDENFITY GLASS LOCA AS PER DRA / BAY NO BROKENGLASS SIZE:1880 X 484 ( ROOF GLASS)QTY 3 NEW GLASS AVABILE BEHIND CURNING BAY 22.10.2020 14:42:04 UTC Yogarajan Pandiyan (QRYPA0)
90607581 | 2020-08-30 | A081-0A8350 | BIO SLUDGE UNIT TRIPPED TO RECTIFY | MX04 | M_X | Schedule Breaker | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10347748 | 700002779390 |  |  | 0 | 16 | 0 | Software fault | Software fault-Suspect software problem | Controller | Check/ Inspect/ Test | 26.08.2020 19:47:19 UTC Mohanraj Chellaih (QRMCH0) Clear description of the problem. OA 8350 BSTD got tripped on emergency trip to be reset PEFS: Prioriteit: Additional mitigations : Requester Name : Mohan Phone : 44032215
90607692 | 2020-09-26 | A081-294XA-50200-S | 2ET-LPU-050 EHT FLT,TROUBLESHOOT* | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10347723 | 700002607282 |  | Instrumentation | 0 | 20 | 20 | Loss of Heating | Loss of Heating-ECM thermostat main circuit failed | Heat Tracing | Hardware Replacement | 26.08.2020 06:32:39 UTC Manik Kalita (QRMKA4) Phone 33695751 Clear description of the problem. 294XA-50200 URGENT COMMON FAIL ALARM STANDING DUE TO 2ET-LPU-050 ISSUE, TO BE CHECK AND IF REQUIRED REPLACE. PEFS: XXX Prioriteit: Additional mitigations : X Insulation Electrical tasks: X JHA needed Requester Name : Manik Kalita Phone : 44032413
90607697 | 2020-10-13 | A081-1SB210N2 | AB_1LFN210N241L304_400W FAULTY LIGHT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10347856 | 700002352082 | ABB MALAYSIA | Electrical | 0 | 12 | 60 | Internal failure / short | Internal failure / short- | Lamps |  | 28.08.2020 20:48:12 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. 1SB210N2-Q52 (Circuit-41) faulty lighting circuit troubleshooting activity under w/o 90606235, found 1LN210N241L304 (400W) lighting fixture faulty need to troubleshoot. Note- power cable disconnected from lighting fixture jb.Area location drg. T-4.013.089 PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : SHYAM TIWARI Phone : 70482542
90608405 | 2020-09-04 | A081-0S0123A | 0S-0123A DP HIGH-PRD, PS | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10348413 | 700002201322 | DKME | Integrity | 0 | 47 | 47 |  |  |  |  | 03.09.2020 09:57:03 UTC Elangovan Muthusamy (QREMU0) 0S-123A DP high filter element to be replaced. 03.09.2020 10:04:22 UTC Bakthavatchalan Thenral (QRBTH0) NOTE:CS-2 is in s/d, hence this filter cleaning is SB , Consulted with PS
90609180 | 2020-09-06 | A081-1SB220N2 | HSSE-LIGHT FIXTURES DAMAGED AC_FINGERS | MX04 | E_SWB_D | Schedule Breaker | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10348535 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 41 | 132 | Mechanical damage | Mechanical damage-Diffusers & fittings damaged | Lighting Fixture |  | 04.09.2020 23:58:34 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. During walk down (Ref.NT No: 10348229)with PTL at AC Area Finger-3 we found Near Reactor(all 7 /8/9) at 1st <(>&<)> 2nd level tube lamp fixtures (36W) and diffusers are damaged and lose of EX integrity. Fixtures and diffusers need to be replaced asap. Light fitting Tag numbers: 1LFN220N223L306 , 1LFN220N222L203, 1LFN220N227L207, 1LFN220N222L210, 1LFN220N222L211, 1LFN220N223L316 PEFS: T-4.013.401, 402, 406, 407 Prioriteit: Additional mitigations : X Scaffold (2 Mtrs Required) Electrical tasks: X E-Disconnect X E-isolation X JHA needed Requester Name : MAGESH Phone : 31548616 05.09.2020 00:08:50 UTC Sudheer Kumar Pendurthi (QRSPE6)
90609193 | 2020-10-03 | A081-1S0241 | 1S-0241 DP INCREASED, REPLACE FILTER | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10348553 | 700002354895 | JFC CORPORATION | Integrity | 955.36 | 60 | 60 |  |  |  |  | 05.09.2020 13:24:20 UTC Balaji Venkatesan (QRBVE6) Clear description of the problem. 1S-0241 FILTER DP INCREASING TREND, NEED TO BE REPLACE THE FILTER ELEMENT. BACKWASH DONE EARLIER WITH THAT FILETR. PEFS: T-13.370.089 Prioriteit: Requester Name : BALAJI Phone : 44032111 06.09.2020 04:43:23 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90609357 | 2020-10-03 | A081-1SB210N2 | TUBE LIGHTS BUSTED,1R-3025 | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10348640 | 700002352082 | ABB MALAYSIA | Electrical | 0 | 22 | 288 | end of life | end of life- | Lighting Fixture | Replace | 07.09.2020 00:37:45 UTC Ahamad Basha (QRABA9) Clear description of the problem. PROACTIVE WALK DOWN IN 1R-3025 FOR CCO WE FOUND THE FLOWING BUSTED TUBE LIGHTS. TO BE REPLACED. -210E104L120 - NEAR 1R-3026 THERMOSYPHON VALVE (WEST SIDE) -1LFN210N215L210 - NEAR 1R-3025 S12 SPADE -1LFN210N215L309 - NEAR 1R-3026 TOP MANWAY (SOUTH SIDE) -1LFN210N215L109 - NEAR 1R-3024 THERMOSYPHON VALVE (NORTH SIDE) -1LFN210N221L314 - NEAR 1R-3026 THERMOSYPHON VALVE (EAST SIDE) -1LFN210N221L315 - NEAR 1R-3026 THERMOSYPHON VALVE (WEST SIDE) -1LFN2101224L322 - NEAR 1R-3023 THERMOSYPHON VALVE (EAST SIDE) -1LFN210N214L218 / 217 - IN BETWEEN 1R3023 - 1R3024 STAIRCASE. -1R3025/1R3026 STEM DRUM RV-1 SOUTH AND EAST SIDE - 4NO'S PEFS: Prioriteit: Additional mitigations : X Use moveable platform or man lift Electrical tasks: X JHA needed Requester Name : AHAMAD BASHA Phone : 44032314 08.09.2020 12:51:47 UTC Mohammad Alam (QRMANR)
90609362 | 2020-09-15 | A081-2SB200N2 | T2-GTL Comfort shelter Light not working | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10348612 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 8 | 4 | Internal failure / short | Internal failure / short- | Lamps | Repair / correct | 06.09.2020 20:46:36 UTC Chon Sung Ong (QRCON0) Clear description of the problem. Train-2 GTL comfort shelter Light not working. PEFS: Prioriteit: Additional mitigations : Requester Name: Ong Chon Sung Phone: 44032311 07.09.2020 01:43:20 UTC Chon Sung Ong (QRCON0) *Also Always Tripped
90609941 | 2020-10-26 | A081-0A8350 | BSTD BAY4 ZONE A ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10349012 | 700002779390 |  |  | 0 | 276 | 290 | Material defect | Material defect- | Other - please specify in text field | Replace | 12.09.2020 12:13:24 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. BAY NO4,ZONE A ROOF TOP 2NOS GLASS BROKEN.TO BE RECTIFIED. PEFS: Prioriteit: Additional mitigations : Requester Name : RAJA RAMASAMY Phone : 44032215 15.10.2020 01:51:45 UTC Yogarajan Pandiyan (QRYPA0) 3 no of glasses replaced in Zone A.
90609943 | 2020-10-15 | A081-0A8350 | BSTD BAY4 ZONE B ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10349013 | 700002779390 |  |  | 0 | 226 | 242 | Material defect | Material defect- | Other - please specify in text field | Replace | 12.09.2020 12:16:53 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. BAY NO4,ZONE B ROOF TOP 1NOS GLASS BROKEN.TO BE RECTIFIED. PEFS: Prioriteit: Additional mitigations : Requester Name : RAJA RAMASAMY Phone : 44032215 15.10.2020 01:58:36 UTC Yogarajan Pandiyan (QRYPA0) 4 Roof glasses replaced in B zone
90609944 | 2020-10-19 | A081-0A8350 | BSTD BAY7 ZONE A ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10349014 | 700002779390 |  |  | 0 | 269 | 242 | Material defect | Material defect- | Other - please specify in text field | Replace | 12.09.2020 12:20:23 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. BAY NO7,ZONE A ROOF TOP 1NOS GLASS BROKEN.TO BE RECTIFIED. PEFS: Prioriteit: Additional mitigations : Requester Name : RAJA RAMASAMY Phone : 44032215 26.10.2020 01:24:28 UTC Yogarajan Pandiyan (QRYPA0) Total of 25 no of Roof glasses replaced in the WOs 90609944, 90593049, 90606046
90609945 | 2020-10-15 | A081-0A8350 | BSTD BAY8 ZONE B ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10349016 | 700002779390 |  |  | 0 | 220 | 242 | Material defect | Material defect- | Other - please specify in text field | Replace | 12.09.2020 12:23:59 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. BAY NO 8,ZONE B ROOF TOP 1 NOS GLASS BROKEN.TO BE RECTIFIED. PEFS: Prioriteit: Additional mitigations : Requester Name : RAJA RAMASAMY Phone : 44032215 15.10.2020 01:45:37 UTC Yogarajan Pandiyan (QRYPA0) ALL THE BROKEN GLASSES REPLACED ON 13.10.2020
90610217 | 2020-10-28 | A081-0A8350 | BSTD BAY1 ZONE B ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10349110 | 700002779390 |  |  | 0 | 213 | 227 | Other - please specify in text field | Other - please specify in text field-glasses broken | Other - please specify in text field | Replace | 14.09.2020 08:18:11 UTC Gnana Patrici Zacharias (QRGZA0) Clear description of the problem. BSTD Bay -1 zone B one roof glass broken. PEFS: Prioriteit: Additional mitigations : X Use moveable platform or man lift X JHA needed Requester Name : PATRIC Phone : 44032215 27.10.2020 23:39:11 UTC Arunbhai Patel (QRAPA0) Total of 19 no of Roof Glasses Replaced in WO no 90593048/90609920/90610624/90610217
90610219 | 2020-10-09 | A081-0A8350 | BSTD BAY6 ZONE B ROOF GLASS CHANGE | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10349113 | 700002779390 |  |  | 0 | 186 | 242 | Other - please specify in text field | Other - please specify in text field-two glass broken | Other - please specify in text field | Replace | 14.09.2020 08:31:06 UTC Gnana Patrici Zacharias (QRGZA0) Clear description of the problem. BSTD Bay- 6 zone B two roof glass broken PEFS: Prioriteit: Additional mitigations : X Use moveable platform or man lift X JHA needed Requester Name : PATRIC Phone : 44032215 09.10.2020 09:18:53 UTC Arunbhai Patel (QRAPA0) Replaced two new glass
90610413 | 2020-11-07 | A081-2SB210N2 | BUSTED TUBE LIGHTS, GTL2, HPS-1ST STAGE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10349420 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 4 | 8 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 16.09.2020 19:30:16 UTC Sonny Mendoza (QRSME3) Clear description of the problem. Around 33x2 tube lights are busted in first <(>&<)> second elevation at train2 HPS 1st stage reactors. NOte: This locations are priority as required on FO routine sampling and adjustment activity, CCO/ROR Spading and despading activity. PEFS: T-4.013.090 Prioriteit: Additional mitigations :
90610624 | 2020-10-28 | A081-0A8350 | BSTD BAY1 ZONE B ROOF GLASS BROKEN | MX04 | M_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10349553 | 700002779390 |  |  | 0 | 213 | 227 | Other - please specify in text field | Other - please specify in text field-glasses broken | Other - please specify in text field | Replace | 19.09.2020 00:36:45 UTC Vijay Muthukumaresan (QRVMU2) Clear description of the problem. IN BSTD BAY NO 1, ZONE B 2 NUMBERS ROOF GLASS BROKEN CONDITION. TO BE CHANGED PEFS: Prioriteit: Additional mitigations : X Use moveable platform or man lift X JHA needed Requester Name : VIJAY Phone : 44032215 27.10.2020 23:35:41 UTC Arunbhai Patel (QRAPA0) Total of 19 no of Roof Glasses Replaced in WO no 90593048/90609920/90610624/90610217
90610998 | 2020-09-23 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT-PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10349796 | 700002200042 | DKME | Integrity | 0 | 47.1 | 47.1 |  |  |  |  | 22.09.2020 11:03:57 UTC Sunil Kumar Puliyath (QRPSU4) Clear description of the problem. UNIT-100, STR#3 0S-163A FILTER DP HIGH. NEED TO REPLACE THE FILTER ELEMENTS PEFS: T-4.094.342 Prioriteit: Additional mitigations : X JHA needed Requester Name : SUNIL PULIYATH Phone : 44032115
90611048 | 2021-01-31 | A081-0A8350 | EXTVENDOR: BSTD ODOUR METER CALIBRATION | MX09 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10349738 | 700002779390 |  | Integrity | 3680.31 | 0 | 0.1
90611049 | 2020-11-15 | A081-0A8350 | BSTD BAY1 ZONE A SIDE WALL GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10349803 | 700002779390 |  | Integrity | 7756.96 | 209 | 209 | Material defect | Material defect- | Other - please specify in text field | Replace | 22.09.2020 13:10:11 UTC Gnana Patrici Zacharias (QRGZA0) Clear description of the problem. BSTD BAY-1 ZONE A ONE WALL GLASS BROKEN (NORTH WEST SIDE) PEFS: Prioriteit: Additional mitigations : X Use moveable platform or man lift
90612720 | 2020-10-05 | A081-2A8324 | 2A 8324 SMALL WHEEL DAMAGE | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10350716 | 700002297332 |  | Integrity | 0 | 8 | 8 |  |  |  |  | 03.10.2020 08:29:12 UTC Shinde Villas (QRSVI3) Clear description of the problem. 2A 8324 DAF SMALL WHEEL IS DAMAGE NEED TO REPLACE PEFS: T-4.118.864 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X Scaffold Electrical tasks: Requester Name : VILAS SHINDE Phone : 44032215 04.10.2020 07:38:55 UTC Raju Sutham (QRRSU3) DURING THIS TIME SIX MONTH PM JOB WO 90610214 NEED TO CLUB, REFER THE WORKORDER 90610214, BOTH JOBS NEED TO CLUB TOGETHER. 09.10.2020 11:58:43 UTC Madhan Subramani (QRMSUA) removed damaged wheel install new wheel job completed
90613271 | 2020-10-15 | A081-2SB200N2 | FS-T2BA Exchanger side Light not working | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10351062 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 4 | 2 | end of life | end of life- | Lamps | Check/ Inspect/ Test | 07.10.2020 15:49:04 UTC Chon Sung Ong (QRCON0) Clear description of the problem. T2- BA area, Exchanger side all Floor normal light not working. only emergency light was glowing. Reactor, Fin fans and LES was working properly PEFS: Prioriteit: Additional mitigations : Requester Name: Ong Chon Sung Phone: 44032311 08.10.2020 04:33:46 UTC Srinivasa Dandu (QRSDA3) THIS SAP IS TO DI INITIAL CHECK FOLLOWED BY NEW SAP FOR CORRECTIVE REPAIR 15.10.2020 12:04:28 UTC Sudheer Kumar Pendurthi (QRSPE6) We Created common notification --10351706 for lamps replacement actiivty, hence close this WO
90613356 | 2021-05-30 | A081-0A8350 | BSTD ROOF CLEANER PLC EMERGENCY SWITCH | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10351035 | 700002779390 |  | Integrity | 0 | 0 | 0
90613575 | 2020-10-11 | A081-1A8324 | TR1 DAF SMALL WHEEL DAMAGED TO B FIX NEW | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10351098 | 700002348718 |  | Integrity | 767.45 | 86 | 86 |  |  |  |  | 08.10.2020 01:05:11 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. TR1 DAF SCRAPPER ARM SMALL WHEEL DAMAGED ,NEED TO REPLACE AS SOON AS POSSIABLE,TOO MUCH NOISE OBSERVED,SEEMS BEARING DAMAGED...TO BE FIXED NEW WHEEL. PEFS: Prioriteit: Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-isolation Requester Name : RAJA RAMASAMY Phone : 44032215 11.10.2020 06:45:20 UTC Raju Sutham (QRRSU3) DAF1, The small wheels were found damaged, the abnormal noise was observed from the damaged wheel. The lining of the wheel’s was found peel off and it can fail any time . The small wheels are frequently damaging due to ambient and size of the wheel. Kindly advise AMT to replace all four wheels. 15.10.2020 01:14:28 UTC Madhan Subramani (QRMSUA) DAMAGED WHEEL REMOVED AND INSTALL NEW WHEEL.JOB COMPLETED
90613663 | 2020-10-13 | A081-2A8324 | Tr2 DAF Small Wheel Damaged | MX04 | M_X_X | Schedule Breaker | 0 |  | FLOTATOR PACKAGE | CM | ETP | 10351316 | 700002297332 |  | Integrity | 767.44 | 0 | 0 |  |  |  |  | 11.10.2020 08:17:56 UTC Ron Sorreno (QRRSO1) Clear description of the problem. Train2 DAF (2A-8324)small wheel found out damaged condition. Attached pictures provided. PEFS: T-4.118.867 Prioriteit: Additional mitigations : X WPS/ Work instruction needed X Scaffold Electrical tasks: X JHA needed Requester Name : VILLAS SHINDE Phone : 44032215 15.10.2020 01:07:31 UTC Madhan Subramani (QRMSUA) dAMAGED WHEEL REMOVED AND FIX NEW WHEEL.JOB COMPLETED.
90613942 | 2020-10-31 | A081-2SB210N2 | 2R-3022 Area light not working | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10351541 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 36.1 | 150.1 | end of life | end of life- | Lamps | Replace | 13.10.2020 22:08:02 UTC Arvindkumar Mohanlal Patel (QRAPA3) Clear description of the problem. 2R-3022 area poor lighting details are below 1) Ground floor 2R-3022 Wax outlet line both side Two light not working. 2) First floor 2R-3022 Man way both side Two light not working. 3) First floor 2R-3022 Effluent outlet line <(>&<)> near LT One light not working. 4) Top floor 2R-3022 Man way both side Two light not working. PEFS: Prioriteit: Additional mitigations : X Scaffold Requester Name : Arvindkumar patel Phone : 44032311 18.10.2020 16:46:40 UTC Mohammad Alam (QRMANR) 36W <(>&<)> 18W LAMP AVAILABLE IN HAND.
90614299 | 2021-01-23 | A081-2SB200N2 | BA AREA FAULTY 36w/18w LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10351706 | 700002373557 | ABB MALAYSIA | Electrical | 4306.93 | 66 | 226 | end of life | end of life- | Lamps |  | 15.10.2020 12:01:56 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. DURING YEARLY LIGHTING INSPECTION (90582062)FOUND MANY LAMPS ARE NOT WORKING AT U23100,U23200 EXCHANGER SIDE (ALL FLOORS) AND MAINPIPERACK. 1)2x36W LIGHT FITTING LAPMS--120 No's) 2)2X18W LIGHT FITTING LAPMS- 110 No's) 3)36W DIFFUSERS--3 No's PEFS:
90615474 | 2020-12-13 | A081-2SB210N2 | BUSTED TUBE LIGHTS, GTL2, WDU Area | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10352162 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 0 | 0.1 | end of life | end of life- | Lamps | Repair / correct
90615791 | 2020-12-15 | A081-2A8324 | TR-2 DAF SCRAPPER SMALL WHEEL DAMAGED | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10352424 | 700002297332 |  | Rotating | 254.46 | 86 | 86
90615910 | 2020-12-27 | A081-2SB210N2 | PMFLT-2SB210N2-CKT-41 & 16 TROUBLESHOOT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10352534 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 16.1 | 20.1 | Internal failure / short | Internal failure / short- | Power Supply | Repair / correct
90615913 | 2020-12-15 | A081-2SB210N2 | BB AREA FAULTY 36w/18w LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10352532 | 700002373562 | ABB MALAYSIA | Electrical | 1047.65 | 122 | 286 | end of life | end of life- | Lamps
90617947 | 2020-12-17 | A081-0S0123A | 0S-0123A DP HIGH-> | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10352673 | 700002201322 | DKME | Integrity | 0 | 27 | 47
90617950 | 2020-11-14 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10352674 | 700002200043 | DKME | Integrity | 0 | 27 | 47 |  |  |  |  | 29.10.2020 12:18:06 UTC Elangovan Muthusamy (QREMU0) 0S-163B DP high filter element to be replaced.
90618115 | 2020-12-28 | A081-2SB210N2 | BB_AREA FAULTY 400W LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10352928 | 700002373562 | ABB MALAYSIA | Electrical | 278.2 | 80 | 720 | end of life | end of life- | Lamps | Replace
90618116 | 2020-12-26 | A081-2SB210N2 | BB_AREA FAULTY 400W LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10352930 | 700002373562 | ABB MALAYSIA | Electrical | 301.39 | 72 | 486 | end of life | end of life- | Lamps
90618117 | 2020-12-31 | A081-2SB210N2 | BB_AREA FAULTY 250W LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10352943 | 700002373562 | ABB MALAYSIA | Electrical | 88.07 | 40 | 300 | end of life | end of life- | Lamps | Replace
90618118 | 2020-12-06 | A081-2SB210N2 | BB_AREA FAULTY 150W LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10352945 | 700002373562 | ABB MALAYSIA | Electrical | 27.9 | 16 | 120 | end of life | end of life- | Lamps
90618400 | 2020-11-18 | A081-0A8350 | BSTD BAY-5 ONE ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10353281 | 700002779390 |  | Integrity | 42.31 | 0 | 227 | Other - please specify in text field | Other - please specify in text field-GLASS BROKEN | Other - please specify in text field | Replace | 04.11.2020 01:24:24 UTC Gnana Patrici Zacharias (QRGZA0) Clear description of the problem. BSTD bay 5 zone B one roof glass broken PEFS: Prioriteit: Additional mitigations : X Scaffold
90618869 | 2020-11-22 | A081-0S0123A | 0S-0123A/B EHT thermostate to be fixed | MX04 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10353428 | 700002201322 | DKME | Integrity | 0 | 6 | 6 | Normal Wear | Normal Wear-Removed due to vibration | Supports | Fix / Repair | 05.11.2020 06:42:49 UTC Muhammad Imran (QRMIM0) Clear description of the problem. 0S-0123a/B EHT thermosate 4 no. are hanging to be fixed properly. PEFS: Prioriteit: Additional mitigations : X Insulation
90618894 | 2020-12-27 | A081-1SB220N2 | AC AREA FAULTY 36w/18w LAMPS REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10353423 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 16 | 322 | end of life | end of life- | Lamps
90618902 | 2020-11-22 | A081-FIRE HYDRANT | WTR AREA FH-141 CAM ASSEMBLY DAMAGED | MX04 |  | Routine Wrk Lvl 2 | 0 |  | FIRE HYDRANT | CM | UTL | 10353465 |  |  |  | 145.18 | 4 | 4 |  |  |  |  | 05.11.2020 11:34:34 UTC Leo Gaigher (QRLGA0) Clear description of the problem. As part of the bi-annual hydrant inspection conducted by FIT in October 2020 for UTL Water/ETP, it was found that the Winged Cam Assembly Kit at the left-hand side 2.5" outlet at hydrant FH141 was seized. The spare part MM number is 10687723. FH141 is located in Road E opposite Sub Station OSS 500. PEFS, location, specification details will be forwarded to OMC. PEFS: Prioriteit:
90619997 | 2020-12-26 | A081-0A8350 | BSTD BAY- 4 ROOF GLASS 4 NOS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10353988 | 700002779390 |  | Integrity | 3.99 | 105 | 197 | Other - please specify in text field | Other - please specify in text field-GLASS BROKEN | Other - please specify in text field | Replace
90620201 | 2020-11-12 | A081-0S0143A | 0S-0143A FILTER DP HIGH | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10354146 | 700002201324 | DKME | Integrity | 21316.85 | 27 | 47 |  |  |  |  | 10.11.2020 12:23:45 UTC Sivakumar Manokaran (QRSMAA) 0S-0143A filter DP high need to repalce the filter element. 12.11.2020 08:55:42 UTC Bakthavatchalan Thenral (QRBTH0) Note:Level-1 NO is changed to SB , due to CS-1 S/D (0K-0135 S/D)
90620521 | 2021-07-05 | A081-0S0163B | 0S-0163B HC FILTER ELEMENT TO BE REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10354368 | 700002200043 | DKME | Integrity | 4177.81 | 47 | 47
90620654 | 2020-12-16 | A081-2SB210N2 | 2R-3026 Ist&2nd floor lights not working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10354552 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 0 | 0.1 | end of life | end of life- | Lamps | Replace
90620686 | 2020-12-14 | A081-0S8361A | SDU-A FEED SIDE DRAIN HOSE DETACHED | MX04 | M_ROT_CENT | Routine Wrk Lvl 4 | 0 |  | CENTRIFUGE | CM | ETP | 10354373 | 700001729713 |  | Rotating | 549.3 | 20 | 20
90621180 | 2020-11-22 | A081-1SB210N2 | BUSTED TUBE LIGHTS,1R-3023 REACTOR SIDE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10354722 | 700002352082 | ABB MALAYSIA | Electrical | 0 | 4 | 4.1 |  |  |  |  | 17.11.2020 21:53:31 UTC Ahamad Basha (QRABA9) Clear description of the problem. Reactor 1R-3023 ‘Next ROR’ Proactive walkdown carried out for lightings on 17 November 2020, found some tube lights are busted at different level of reactor side. Below mentioned tag’s tube lights are to be replaced. 1R-3023 SECOND FLOOR: 1LFE210E101L113 - East side of 130FC-33006/VC 1R-3023 THIRD FLOOR:
90621298 | 2020-12-03 | A081-1SB220N2 | Poor lighting on 1F8401 stack elevation | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10354281 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 0 | 8 | end of life | end of life- | Lamps | No action
90621324 | 2020-12-17 | A081-2SB210N2 | Busted,tube light,topMW of 2R3022 | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10352908 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 0 | 0.1 | end of life | end of life- | Lamps | Replace
90623718 | 2021-01-06 | A081-0A8350 | BSTD BAY-3 ROOF GLASS REPLACEMENT | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10356267 | 700002779390 |  | Integrity | 1668.95 | 172 | 171 | Mechanical damage | Mechanical damage- | Other - please specify in text field | Replace | 27.11.2020 23:49:23 UTC Vijay Muthukumaresan (QRVMU2) Clear description of the problem. In BSTD/BAY3/ZONEA ONE ROOF GLASS FOUND BROKEN. IT IS LOCATED IN HEAP NO 4, AND THE ROW NO IS 27. REFER ATTACHED DRAWING FOR THE EXACT LOCATION IN ROOF. PEFS: T-4.804.771 Prioriteit: Additional mitigations :
90623719 | 2020-12-14 | A081-0A8350 | BSTD BAY-4 ROOF GLASS REPLACEMENT | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10356269 | 700002779390 |  | Integrity | 0 | 213 | 227 | Other - please specify in text field | Other - please specify in text field-GLASS BROKEN | Roof | Replace
90626201 | 2021-01-04 | A081-1SB220N2 | AC_PRETRETMENT & U8400 AREA 36/18W LAMPS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10357514 | 700002356603 | ABB MALAYSIA | Electrical | 188.26 | 18 | 24 | end of life | end of life- | Lamps |  | 08.12.2020 08:45:35 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. ON REF. WO:90618894, 90598750 WE ARE SPLITTING AREA WISE, DUE TO EASY FOR CLOSING WO AND BILLING PURPOSE BY NORMS TEAM. 36W/18w LAMPS <(>&<)> DIFFUSERS NEED TO REPLACE AT PRETRETMENT <(>&<)> U8400 AREA. LAMPS 36W --110 No's, 18W-40No's <(>&<)> DIFFUSERS 36W-3 <(>&<)> 18W-2 Note : ALL MATERIALS IN HAND PEFS:
90626202 | 2021-01-13 | A081-1SB220N2 | AC_PIPERACK & FINFAN AREA 36/18W LAMPS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10357513 | 700002356603 | ABB MALAYSIA | Electrical | 96.36 | 22 | 76 | end of life | end of life- | Lamps |  | 08.12.2020 08:41:37 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. ON REF. WO:90618894, 90598750 WE ARE SPLITTING AREA WISE, DUE TO EASY FOR CLOSING WO AND BILLING PURPOSE BY NORMS TEAM. 36W/18w LAMPS <(>&<)> DIFFUSERS NEED TO REPLACE AT MAIN PIPERACK <(>&<)> FINFAN AREA. LAMPS 36W --100 No's, 18W-80No's <(>&<)> DIFFUSERS 36W-5 <(>&<)> 18W-3 Note : ALL MATERIALS IN HAND PEFS: Prioriteit:
90626203 | 2021-01-03 | A081-1SB220N2 | AC_FURNACE AREA 36/18W LAMPS & DIFFUSERS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10357509 | 700002356603 | ABB MALAYSIA | Electrical | 485.65 | 40 | 48 | end of life | end of life- | Lamps |  | 08.12.2020 08:26:32 UTC Sudheer Kumar Pendurthi (QRSPE6) ON REF. WO:90618894, 90598750 WE ARE SPLITTING AREA WISE, DUE TO EASY FOR CLOSING WO AND BILLING PURPOSE BY NORMS TEAM. 36W/18w LAMPS <(>&<)> DIFFUSERS NEED TO REPLACE AT FURNISH <(>&<)> DMDS AREA (STRING 1<(>&<)>2), LAMPS 36W --80 No's, 18W-100No's <(>&<)> DIFFUSERS 36W-4 <(>&<)> 18W-5 Note : ALL MATERIALS IN HAND PEFS: Prioriteit:
90626204 | 2021-01-19 | A081-1SB220N2 | AC_FINGERS AREA 36/18W LAMPS & DIFFUSERS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10357507 | 700002356603 | ABB MALAYSIA | Electrical | 166.38 | 12 | 24 | end of life | end of life- | Lamps | Replace | 08.12.2020 08:13:41 UTC Sudheer Kumar Pendurthi (QRSPE6) Clear description of the problem. ON REF. WO:90618894, 90598750 WE ARE SPLITTING AREA WISE, DUE TO EASY FOR CLOSING WO AND BILLING PURPOSE BY NORMS TEAM. 36W/18w LAMPS <(>&<)> DIFFUSERS NEED TO REPLACE AT REACTORS SIDE (ALL 3 FINGERS), LAMPS 36W --150 No's, 18W-80No's <(>&<)> DIFFUSERS 36W-8 <(>&<)> 18W-5 Note : ALL MATERIALS IN HAND PEFS: Prioriteit:
90626411 | 2021-01-19 | A081-1F5111 | 1F5111,OBSERVATION WINDOW GLASS BROKEN | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10358083 | 700002348459 | KTI | Integrity | 1899.87 | 17 | 18 | Design Error | Design Error-high temparature | Glass section | Replace
90626685 | 2021-04-12 | A081-1SB220N2 | 1SB220N2 FAULTY SPACE HEATER REPLACE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10358155 | 700002356603 | ABB MALAYSIA | Electrical | 780.13 | 16.5 | 16.5 | end of life | end of life- | Heating element | Replace
90626973 | 2021-02-07 | A081-2SB210N2 | 2R-3029,1st&2nd floor lights not working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10358532 | 700002373562 | ABB MALAYSIA | Electrical | 79.24 | 4 | 12 | end of life | end of life- | Lamps | Replace
90627174 | 2021-02-10 | A081-1SB210N2 | lighting not working, AB 1R-3023 area | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10358533 | 700002352082 | ABB MALAYSIA | Electrical | 0 | 4 | 12 | end of life | end of life- | Lamps | Replace
90627199 | 2020-12-28 | A081-0X0104 | 0S0104 CONVEYOR CLEANING REQUIRED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10358717 | 700002206193 |  | Electrical | 0 | 6 | 12 | Fouling | Fouling- | drive system | Cleaned
90627204 | 2021-01-07 | A081-294XA-50200-S | 2ET-LPU-055 (246RV-10001)EHT FLT,ALARM** | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10358416 | 700002607282 |  | Instrumentation | 877.48 | 82 | 114 | Loss of Heating | Loss of Heating-Main & Redudant Thermostat failed | Heat Tracing | Hardware Replacement | 15.12.2020 23:12:35 UTC Deepak Sathiya Moorthy (QRDMO5) Clear description of the problem. 2ET-LPU-055 at 246RV-10001 platform had alarm in Substation, Checked in Field and Switch Changed over from Main to Redundant, Reset done in substation. Again Alarm started in Substation. EHT Fault Alarm to be checked and rectified. PEFS: Prioriteit: Electrical tasks: Requester
90627223 | 2021-03-28 | A081-1F5111 | 1F-5111,FLAPPER,WG 2,HIGH TEMP,MOC 91431 | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10358410 | 700002348459 | KTI | Integrity | 1835.58 | 0 | 115 | Operating outside design | Operating outside design-Excess temp zone | Glass section | Replace | 15.12.2020 20:34:06 UTC Patrick Tirso Alegria (QRPAL0) Clear description of the problem. During window flapper temperature survey on 15/12/20 NS, W-G2 temperature reading > 500 deg C (567 degC). For integrity inspection/r epair. Visual appearance of the flapper not in red hot condition PEFS: Prioriteit: Additional mitigations :
90627940 | 2021-03-23 | A081-1SB210N2 | 1SB210N2 FAULTY SPACE HEATER | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10359125 | 700002352082 | ABB MALAYSIA | Electrical | 1508.93 | 8 | 8 | end of life | end of life- | Heating element | Replace | 21.12.2020 11:00:48 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING THERMOSTAT SETTING FOR SPACE HEATER UNDER MOC-83820 FOUND 1SB210N2-1/2/3 CABLE COMPARTMENT SPACE HEATER NOT WORKING NEED TO T ROUBLESHOOT/REPLACE MATERIAL NO. FOR SPACE HEATER 10539597- 03 NOS. REQUIRED MATERIAL NO. FOR CONTROL FUSE 10537966(2A)- 03 NOS. PEFS: Prioriteit: Additional mitigations : Electrical tasks:
90628217 | 2021-07-28 | A081-1SB220N2 | 1LFN220N208L111 36W LIGHT FIXTURE DAMAGE | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360678 | 700002356603 | ABB MALAYSIA | Electrical | 70.09 | 10 | 33 | end of life | end of life- | Lighting Fixture | Replace
90628218 | 2021-08-23 | A081-1SB220N2 | 1LFN220N208L309 36W LIGHT FIXTURE DAMAGE | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360697 | 700002356603 | ABB MALAYSIA | Electrical | 144.5 | 8 | 33 | end of life | end of life- | Lighting Fixture | Replace | 24.12.2020 10:25:14 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING LAMP REPLACEMENT FOUND 1LFN220N208L309 LIGHTING FIXTURE 36W NOT WORKING NEED TO REPLACE PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X JHA needed Requester Name : SHYAM TIWARI Phone : 70482757
90628220 | 2021-08-22 | A081-1SB220N2 | 1LFN220N227L110 36W LIGHT FIXTURE DAMAGE | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360699 | 700002356603 | ABB MALAYSIA | Electrical | 113.86 | 8 | 33 | end of life | end of life- | Lighting Fixture | Replace | 24.12.2020 10:34:23 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING LAMP REPLACEMENT FOUND 1LFN220N227L110 LIGHTING FIXTURE 36W NOT WORKING NEED TO REPLACE. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X JHA needed Requester Name : SHYAM TIWARI Phone : 70482757
90628221 | 2021-08-01 | A081-1SB220N2 | 1LFN220N227L207 36W LIGHT FIXTURE FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360704 | 700002356603 | ABB MALAYSIA | Electrical | 126.56 | 8 | 33 | end of life | end of life- | Lighting Fixture | Replace | 24.12.2020 10:41:00 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING LAMP REPLACEMENT FOUND 1LFN220N227L207 LIGHTING FIXTURE 36W NOT WORKING NEED TO REPLACE. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X JHA needed Requester Name : SHYAM TIWARI Phone : 70482757
90628222 | 2021-09-12 | A081-1SB220N2 | 1LFN220N227L107 36W LIGHT FIXTURE FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360709 | 700002356603 | ABB MALAYSIA | Electrical | 126.98 | 8 | 33 | Operating at high temperature | Operating at high temperature-NR REACTOR, SO HIGH AMBIENT TEMP. | Lighting Fixture | Replace
90628350 | 2021-09-13 | A081-1SB220N2 | 1LFN220N223L105 36W LIGHT FIXTURE FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360845 | 700002356603 | ABB MALAYSIA | Electrical | 263.34 | 8 | 33 | end of life | end of life- | Lighting Fixture | Replace
90628351 | 2021-08-30 | A081-1SB220N2 | 1LFN220N222L203 36W LIGHT FIXTURE FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360846 | 700002356603 | ABB MALAYSIA | Electrical | 113.86 | 8 | 47 | end of life | end of life- | Lighting Fixture | Replace | 27.12.2020 07:14:45 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING LAMP REPLACEMENT FOUND 1LFN220N222L203 LIGHTING FIXTURE 36W NOT WORKING NEED TO REPLACE PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X JHA needed Requester Name : SHYAM TIWARI Phone : 70482757
90628353 | 2021-08-28 | A081-1SB220N2 | 1LFN220N222L304 36W LIGHT FIXTURE FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360848 | 700002356603 | ABB MALAYSIA | Electrical | 107.09 | 8 | 33 | end of life | end of life- | Lighting Fixture | Replace | 27.12.2020 07:23:33 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING LAMP REPLACEMENT FOUND 1LFN220N222L304 LIGHTING FIXTURE 36W NOT WORKING NEED TO REPLACE PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X JHA needed Requester Name : SHYAM TIWARI Phone : 70482757
90628354 | 2021-09-12 | A081-1SB220N2 | 1LFN220N222L106 36W LIGHT FIXTURE FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360850 | 700002356603 | ABB MALAYSIA | Electrical | 147.71 | 8 | 33 | Premature failure | Premature failure-WORKING AT HIGH AMBIENT TEMP NR. REACTOR | Lighting Fixture | Replace
90628760 | 2021-02-11 | A081-1SB210N2 | PMFLT_AB_PIPERACK & FINFAN 36/18W LAMPS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10361504 | 700002352082 | ABB MALAYSIA | Electrical | 2767.48 | 72 | 48 | end of life | end of life- | Lamps
90628761 | 2021-02-22 | A081-1SB210N2 | PMFLT_AB_REACTORS SIDE 36/18W LAMPS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10361506 | 700002352082 | ABB MALAYSIA | Electrical | 4948.19 | 72 | 48 | end of life | end of life- | Lamps
90628762 | 2021-02-08 | A081-1SB210N2 | PMFLT_AB_EXCHANGERS SIDE 36/18W LAMPS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10361507 | 700002352082 | ABB MALAYSIA | Electrical | 3817.49 | 48 | 48 | end of life | end of life- | Lamps
90628763 | 2021-02-27 | A081-1SB210N2 | PMFLT_AB_UNIT-13400 AREA 36/18W LAMPS | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10361508 | 700002352082 | ABB MALAYSIA | Electrical | 3301.03 | 37 | 32 | end of life | end of life- | Lamps
90628955 | 2021-01-10 | A081-0S0163A | 0S-0163A FILTER DP HIGH NEED TO REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10363538 | 700002200042 | DKME | Integrity | 150.74 | 27 | 47 |  |  |  |  | 31.12.2020 01:05:21 UTC Sivakumar Manokaran (QRSMAA) 0S-0163A filter DP high need tor epalce the filter element
90629199 | 2021-02-02 | A081-1SB220N2 | 1C-1201 Column poor lightings | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10364450 | 700002356603 | ABB MALAYSIA | Electrical | 212.99 | 6 | 8 | end of life | end of life- | Lamps | Replace
90629213 | 2021-01-02 | A081-0S0123A | 0S-0123A HC FILTER REPLACEMENT-PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10364340 | 700002201322 | DKME | Integrity | 198.83 | 27 | 47 |  |  |  |  | 01.01.2021 16:15:00 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123 A HC FILTER NEEDS CARTRIDGE REPLACEMENT. LOCATION: U-100 STRING-1 (1A1)
90629214 | 2021-01-30 | A081-1F5111 | POOR LIGHTING,1F5111,PENT HOUSE,RECTFY** | MX04 | M_FUR_X | Routine Wrk Lvl 2 | 0 |  | SMR FURNACE | CM | LPU | 10364418 | 700002348459 | KTI | Integrity | 899.21 | 28 | 124 | end of life | end of life- | Lamps | Replace | 02.01.2021 10:49:01 UTC Murugaraj Dharmarajan (QRMDH2) 1F-5111 penthouse area found poor lighting,(1F-5111 Pent house, south side 3 lights and west side 4 lights are not ON, It will be really difficult for Maintenance team to work, if they have to clean burners in dark area.) 19.01.2021 13:46:30 UTC Hareshkumar Chauhan (QRHCH2) 6 numbers 150 watt lamp replaced.for remaining lamps scafolding need to erect. need to add operation
90629223 | 2021-01-17 | A081-0X0104 | 0X-0104 SCREW CONVEYOR CLEANING REQUIRED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10364210 | 700002206193 |  | Electrical | 56.23 | 9 | 12 | Fouling | Fouling- | Other - please specify in text field | Cleaned
90629320 | 2021-09-19 | A081-1SB220N2 | 1LFN220N223L306 36W LIGHT FIXTURE FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10360712 | 700002356603 | ABB MALAYSIA | Electrical | 180.52 | 8 | 26 | end of life | end of life- | Lighting Fixture | Replace
90629329 | 2021-02-13 | A081-2SB210N2 | 2R--3024 lighting not working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10360722 | 700002373562 | ABB MALAYSIA | Electrical | 418.85 | 9 | 12 | end of life | end of life- | Lamps
90629330 | 2021-02-02 | A081-2SB210N2 | 2R-3021 lighting not working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10360725 | 700002373562 | ABB MALAYSIA | Electrical | 661.47 | 8 | 54 | end of life | end of life- | Lamps | Replace
90629766 | 2021-01-06 | A081-2A8324 | TR1 DAF SMALL WHEEL DAMAGE FO1 | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10364635 | 700002297332 |  | Rotating | 322.63 | 12 | 8 | Normal Wear | Normal Wear- | Rotating element | Replace | 04.01.2021 20:02:24 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. TR1 DAF scrapper small wheel damage, rubber came out and hitting other wheel PEFS: Prioriteit: X Scaffold Electrical tasks:
90629789 | 2021-02-28 | A081-0A8350 | BAY3 BSTD ROOF GLASS BROKEN (33QTY) | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10364668 | 700002779390 |  | Integrity | 5332.05 | 231 | 231
90629990 | 2021-01-09 | A081-0S0163B | 0S-0163B FILTER DP HIGH,NEED TO REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10364700 | 700002200043 | DKME | Integrity | 328.49 | 27 | 47
90630269 | 2021-03-20 | A081-0A8350 | BAY1 BSTD ROOF GLASS BROKEN(40TY )OK | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10365604 | 700002779390 |  | Integrity | 9202.46 | 323 | 323
90630320 | 2021-02-04 | A081-2SB210N2 | 2E-3041E lighting not working nrby stair | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10365629 | 700002373562 | ABB MALAYSIA | Electrical | 48.6 | 2 | 4 | end of life | end of life- | Lamps | Replace
90630321 | 2021-02-04 | A081-2SB210N2 | 2R-3011 lighting not working nrby stair | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10365630 | 700002373562 | ABB MALAYSIA | Electrical | 17.52 | 2 | 4 | end of life | end of life- | Lamps | Replace
90630346 | 2021-01-14 | A081-1S0241 | 1S-0241 FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10365665 | 700002354895 | JFC CORPORATION | Integrity | 1225.76 | 27 | 65 |  |  |  |  | 07.01.2021 07:05:50 UTC Rajesh Chandra Sekhara Pillai (QRRPI4) Clear description of the problem. 1S-0241 filter element needs to be replaced as DP is showing decreasing trend even when increasing the flow through the filter. Previously backwashing done many times for this filter PEFS: T-13.370.089 Prioriteit: Clear description of the problem, answer the following questions :
90630374 | 2021-01-18 | A081-0A8350 | BAY NO-3 MAIN DOOR NOT OPENING | MX04 | M_X_X | Schedule Breaker | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10365603 | 700002779390 |  | Integrity | 193.32 | 24 | 0 | Other - please specify in text field | Other - please specify in text field-door not open | Other - please specify in text field | Fix / Repair | 06.01.2021 12:10:28 UTC Shinde Villas (QRSVI3) Clear description of the problem. BAY NO-3 MAIN DOOR NOT OPEN DUE TO WIRE DRUM WIRE BROKEN SO UNABLE TO OPEN IT.NEED MECH HELP. PEFS: Prioriteit: Additional mitigations : X Scaffold X JHA needed
90630513 | 2021-01-16 | A081-0S0123B | 0S-0123B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10365877 | 700002200643 | DKME | Integrity | 256.08 | 27 | 47 |  |  |  |  | 10.01.2021 21:51:36 UTC Sivakumar Manokaran (QRSMAA) 0S-0123B filter DP high need to repalce the filter element
90630792 | 2021-01-26 | A081-0A8350 | BAY9 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10365921 | 700002779390 |  | Integrity | 274.75 | 74 | 74
90632175 | 2021-02-27 | A081-0A8350 | BAY1 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10366948 | 700002779390 |  | Integrity | 3121.54 | 0 | 0
90632176 | 2021-03-01 | A081-0A8350 | BAY2 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10366951 | 700002779390 |  | Integrity | 1806.76 | 0 | 0
90632458 | 2021-02-28 | A081-0A8350 | BAY3 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10367046 | 700002779390 |  | Integrity | 0 | 0 | 0
90632459 | 2021-05-08 | A081-0A8350 | BAY7 BSTD ROOF GLASS BROKEN (31QTY) OK | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10367049 | 700002779390 |  | Integrity | 7944.01 | 227 | 227
90632460 | 2021-04-26 | A081-0A8350 | BAY4 BSTD ROOF GLASS BROKEN (40QTY)OK | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10367048 | 700002779390 |  | Integrity | 4769.01 | 221 | 221
90632492 | 2022-01-29 | A081-0A8350 | BSTD BAY 04 ROOF GLASS REPLACE*40* QTY | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10367116 | 700002779390 |  | Integrity | 23964.42 | 554 | 554
90632500 | 2021-01-24 | A081-2A8324 | DAF2 SMALL WHEELS DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10367213 | 700002297332 |  | Rotating | 650.13 | 8 | 8 | Other - please specify in text field | Other - please specify in text field-damage wheels | Other - please specify in text field | Replace | 21.01.2021 06:15:36 UTC Vasu Sampathkumar (QRVSA0) Clear description of the problem. DAF 2 SCAPPER SMALL WHEELS FRONT INNER AND REAR OUTER BOTH WHEELS DAMAGED. TO BE REPLACED ASAP. PEFS: Prioriteit: Additional mitigations : X WPS/ Work instruction needed
90632807 | 2021-02-21 | A081-1F5111 | 1F5111,W-J2,WINDOW FLAPPER STUCK UP | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10367412 | 700002348459 | KTI | Integrity | 252.68 | 10 | 10 |  | -
90632839 | 2021-03-21 | A081-1F5111 | 1F5111,TUBE ROW HET SHELD DETACHD;ROWB** | MX04 | M_FUR_X | Routine Wrk Lvl 2 | 0 |  | SMR FURNACE | CM | LPU | 10367287 | 700002348459 | KTI | Integrity | 0 | 16 | 16 | Material defect | Material defect- | Other - please specify in text field | Replace | 21.01.2021 21:23:26 UTC Ferdinand Balinos (QRFBA2) Clear description of the problem. 1F-5111 reformer penthouse found that the heat shield on Row B tubes were detached from hook. Checked hook and found one end sheared off. To be fixed. PEFS: NA Prioriteit: Requester Name : Ferdinand Balinos
90632995 | 2021-02-03 | A081-0P2021 | ASU 3 ACC CLEANING PUMP SET UP | MX09 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10367407 | 700002199414 | PRATISSOLI | Rotating | 1407.89 | 16 | 16
90632996 | 2021-02-03 | A081-0P2021 | ASU 7 ACC CLEANING PUMP SET UP | MX09 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10367408 | 700002199414 | PRATISSOLI | Rotating | 0 | 16 | 16
90633178 | 2021-02-04 | A081-1SB210N2 | Lighting to fix 1R3024 | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10367590 | 700002352082 | ABB MALAYSIA | Electrical | 87.63 | 6 | 16 | end of life | end of life- | Lamps | Replace
90633505 | 2021-02-14 | A081-0X0104 | 0X-104 SCREW CONVEYOR CLEANING REQUIRED. | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10367852 | 700002206193 |  | Electrical | 83.21 | 6 | 10 | Fouling | Fouling- | drive system | Cleaned
90633909 | 2021-02-16 | A081-0S0123A | 0S-123A FITER ELEMENT TO BE REPLACD-PRD | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10368079 | 700002201322 | DKME | Integrity | 182.03 | 27 | 47
90633959 | 2021-02-14 | A081-0S8361A | SDU-A SLUDGE LINE COVER BELLOW TEAR OUT | MX04 | M_ROT_CENT | Routine Wrk Lvl 3 | 0 |  | CENTRIFUGE | CM | ETP | 10368009 | 700001729713 |  | Rotating | 2862.65 | 22 | 22
90633967 | 2021-03-02 | A081-0A8350 | BAY3 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10367879 | 700002779390 |  | Integrity | 0 | 4 | 4 |  |  |  |  | 28.01.2021 06:46:14 UTC Shinde Villas (QRSVI3) Clear description of the problem. BAY NO-9 BACKSIDE EMERGENCY DOOR SENSOR CABLE IS MISSING. DISCONNECTED NEED INSTRUMENT/ELECTRICAL SUPPORT PEFS: Prioriteit: Additional mitigations : X Scaffold X JHA needed Requester Name : VILAS SHINDE Phone : 44032215 24.02.2021 07:09:45 UTC Praveen Gowda (QRPGO8) This Job alreday planned under work order no 90629789 , This Notifcation is only for material procument only 08.03.2021 13:33:13 UTC Madhan Subramani (QRMSUA) total 27 glass replaced against wo 90629789 and housekeeping done
90633969 | 2021-03-27 | A081-0A8350 | BAY1 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10367446 | 700002779390 |  | Integrity | 1806.76 | 1 | 1
90633970 | 2021-03-10 | A081-0A8350 | BAY7 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10367447 | 700002779390 |  | Integrity | 0 | 1 | 1
90633971 | 2021-05-08 | A081-0A8350 | BAY5 BSTD ROOF GLASS BROKEN(35QTY) | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10367764 | 700002779390 |  | Integrity | 6552.15 | 187 | 187
90633972 | 2021-03-10 | A081-0A8350 | BAY7 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10367765 | 700002779390 |  | Integrity | 0 | 1 | 1
90634110 | 2021-03-10 | A081-0A8350 | BAY2 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10368213 | 700002779390 |  | Integrity | 0 | 1 | 1 |  |  |  |  | 31.01.2021 11:43:29 UTC Shinde Villas (QRSVI3) Clear description of the problem. BAY NO-2 ROOF GLASS IS BROKEN NEED MECHENICAL SUPPORT PEFS: Prioriteit: Additional mitigations : X Scaffold X JHA needed Requester Name : VILAS SHINDE
90634111 | 2021-03-14 | A081-0A8350 | BAY2&3BSTDZONEB WALL GLASS BROK(5QTY)OK | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10368214 | 700002779390 |  | Integrity | 0 | 1 | 1 |  |  |  |  | 31.01.2021 11:48:36 UTC Shinde Villas (QRSVI3) Clear description of the problem. BAY NO 3 SIDE GLASS BROKEN NEED MECH. SUPPORT PEFS: Prioriteit: Additional mitigations : X Scaffold X JHA needed Requester Name : VILAS SHINDE
90634112 | 2021-03-14 | A081-0A8350 | BAY5 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10368215 | 700002779390 |  | Integrity | 1806.76 | 0 | 0
90634113 | 2021-04-13 | A081-FIRE HYDRANT | TF,LEAK, WAT,Fire Hydrant FH360 | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10367873 |  |  |  | 0 | 2 | 2
90634330 | 2021-02-13 | A081-2SB200N2 | AH 28 5 nos Tubelight not working | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10368551 | 700002373557 | ABB MALAYSIA | Electrical | 35.05 | 6 | 9 | end of life | end of life- | Lamps | Replace
90634668 | 2021-02-16 | A081-1SB220N2 | Internal lighting AH-05 need to replace | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10369460 | 700002356603 | ABB MALAYSIA | Electrical | 52.57 | 8 | 9 | end of life | end of life- | Lamps | Replace
90634781 | 2021-02-07 | A081-0S0163B | 0S-0163B FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10369649 | 700002200043 | DKME | Integrity | 10852.98 | 27 | 47
90634782 | 2021-02-07 | A081-0S0143B | 0S-0143B FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10369650 | 700002202402 | DKME | Integrity | 7060.17 | 27 | 47
90635149 | 2021-02-09 | A081-0P2021 | ACC cleaning pump connection leaking | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10369742 | 700002199414 | PRATISSOLI | Rotating | 0 | 8 | 8 | Normal Wear | Normal Wear- | Casing | Fix / Repair
90635177 | 2021-02-09 | A081-2A8324 | DAF-2 BIG DAMAGE WHEEL TO BE REPLACED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10369913 | 700002297332 |  | Rotating | 6714.18 | 49 | 136 | Other - please specify in text field | Other - please specify in text field-BIG AND SMALL WHEEL DMAMGE | Other - please specify in text field | Replace
90635464 | 2021-07-27 | A081-2SB200N2 | 2LFN200N205L315 LIGHT 36W NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10370040 | 700002373557 | ABB MALAYSIA | Electrical | 65.71 | 8 | 8 | end of life | end of life- | Lighting Fixture | Replace
90635523 | 2021-04-15 | A081-0P2021 | ACC PUMP MAIN SWITCH/ IND LAMPS NOT WORK | MX04 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10370000 | 700002199414 | PRATISSOLI | Rotating | 77.91 | 6 | 6 | Other - please specify in text field | Other - please specify in text field-CORRODED AND LAMPS BROKEN. | Other - please specify in text field | Check/ Inspect/ Test
90636232 | 2021-03-08 | A081-0A8350 | BSTD BAY7 PIVOTE ARM ROD DISCONNECT | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10370329 | 700002779390 |  | Integrity | 274.34 | 64 | 64 |  |  |  |  | 14.02.2021 08:34:26 UTC Shinde Villas (QRSVI3) Clear description of the problem. BAY NO-7 GROUP NO-2 CEILING FAN PIVOT ARM IS DISCONNECTED FROM MAIN ROD NEED MECHENICAL SUPPORT PEFS: Prioriteit: Additional mitigations : X Scaffold X JHA needed Requester Name : VILAS SHINDE Phone : 44032215 28.03.2021 04:12:20 UTC Ashish Khataria (QRAKHB) job done as per PRS.
90636236 | 2021-03-11 | A081-0A8350 | BAY7 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10370228 | 700002779390 |  | Integrity | 2710.14 | 0 | 0
90636693 | 2021-04-03 | A081-0P2021 | JC-ACC cleaning pump recycle union crack | MX04 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10370720 | 700002199414 | PRATISSOLI | Rotating | 996.42 | 2 | 8
90636819 | 2021-02-18 | A081-0S0143A | 0S-0143A HC FILTER REPLACEMENT-SCE | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10370867 | 700002201324 | DKME | Integrity | 0 | 27 | 47
90636820 | 2021-02-23 | A081-0S0163A | 0S-0163A HC FILTER REPLACEMENT-SCE-> | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10370868 | 700002200042 | DKME | Integrity | 402.6 | 27 | 47
90637324 | 2021-03-07 | A081-0A8350 | BAY5 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10370710 | 700002779390 |  | Integrity | 0 | 1 | 1
90637325 | 2021-03-07 | A081-0A8350 | BAY5 BSTD ROOF GLASS BROKEN | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10370822 | 700002779390 |  | Integrity | 0 | 1 | 1
90637740 | 2021-03-09 | A081-2SB210N2 | 2R-3027&3021 LIGHTING ISSUES TO BE FIXED | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10371353 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 9 | 6 | end of life | end of life- | Lamps |  | 22.02.2021 06:32:49 UTC Ramu Bommana (QRRBO3) Clear description of the problem. 2R-3027 REACTOR LIGHTING ISSUES TO BE FIXED FOR IT'S UPCOMING ROR ACTIVITIES. ALL FUSED BULBS ARE TO BE REPLACED AS PER THE ATTACHED LIST. PEFS: T- 4.002.485 Prioriteit: X Scaffold X JHA needed Requester Name : RAMU BOMMANA Phone : 44032470 03.03.2021 13:28:45 UTC Sudheer Kumar Pendurthi (QRSPE6) We repalced some lamps which is accessibility.For remaining lamps Scaffolding required for to replace.
90637954 | 2022-02-07 | A081-0A8350 | BSTD BAY 08 ROOF GLASS REPLACE*40* QTY | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10371392 | 700002779390 |  | Integrity | 15717.71 | 500 | 500
90637955 | 2021-04-18 | A081-0A8350 | BAY9 BSTD ROOF GLASS BROKEN(10 QTY) | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10371478 | 700002779390 |  | Integrity | 5345.82 | 42 | 42
90642059 | 2021-03-22 | A081-2SB210N2 | 2R-3021 S3 lighting not working | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10372356 | 700002373562 | ABB MALAYSIA | Electrical | 66.89 | 6 | 4 | end of life | end of life- | Lamps | Replace | 03.03.2021 01:23:05 UTC Khairul Anuwa Muda (QRKBI0) Clear description of the problem. 2R-3021 S3 lighting not working need to replace immediately for CCO activities PEFS: Prioriteit: Additional mitigations : X Scaffold Requester Name : Khairul Anuwa Muda Phone : 2311 03.03.2021 04:56:34 UTC Ramu Bommana (QRRBO3) Please refer to the attached document for Defective Lighting Locations.
90642902 | 2021-03-15 | A081-2A8324 | TR2 DAF SCRAPPER SMALL WHEEL DAMAGE FO1 | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10373238 | 700002297332 |  | Rotating | 688.84 | 38 | 52 | Poor installation | Poor installation- | Rotating element | Replace | 12.03.2021 21:17:03 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. TR2 DAF scrapper small wheel damage, rubber came out, wheel to be replaced PEFS: T-4.118.864 Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation Requester Name : Bagus Phone : 44032215
90643064 | 2021-03-20 | A081-0S0143B | 0S-0143B FILTER DP HIGH | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373173 | 700002202402 | DKME | Integrity | 0 | 29 | 49 |  |  |  |  | 11.03.2021 15:05:29 UTC Sivakumar Manokaran (QRSMAA) 0S-0143B filter DP high , need to replace the filter elements. 17.03.2021 11:49:50 UTC Bakthavatchalan Thenral (QRBTH0) Note: Thisa WO is chenged to S/B based on PS instruction, other filter DP Is also increasing , DR.M filter is on S/D
90643420 | 2021-03-20 | A081-0S0143A | 0S-0143A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373546 | 700002201324 | DKME | Integrity | 4058.53 | 29 | 49 |  |  |  |  | 17.03.2021 06:50:04 UTC Sivakumar Manokaran (QRSMAA) DEFECT FOUND: 0S-0143A EQUIPMENT FUNCTION: 0S-0143A SUGGESTED FIX REQUIRED: Mechanical MANNING, MATERIAL AND TOOLS REQUIRED: yes LOCATION/ACCESS ISSUES: No access issue. HEALTH, SAFETY <(>&<)> ENVIRONMENTAL CONSIDERATIONS: Nil REASONING BEHIND CMPT RANKING: 1B ANY SHUTDOWN REQUIRED/ISOLATION: Yes OTHER INFO/ATTACHMENTS (Drawings/Photos/Sketches: 0S-0143A filter DP high need to replace the filter elements
90643456 | 2021-03-21 | A081-0S0123B | 0S-0123B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373484 | 700002200643 | DKME | Integrity | 3919.07 | 29 | 49 |  |  |  |  | 16.03.2021 11:15:22 UTC Sivakumar Manokaran (QRSMAA) 0s-0123B filter DP high need to repalce the filter elements.
90643473 | 2021-03-21 | A081-0P2021 | ASU1 ACC CLEANING PUMP WELDING JOINT | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10373501 | 700002199414 | PRATISSOLI | Rotating | 564.26 | 112 | 112 |  |  |  |  | 16.03.2021 13:27:47 UTC Maideen Kaja (QRMKA9) Clear description of the problem. ASU1 ACC Cleaning Pump Recycle Buffer chamber welding joint leak observed. Please check and to be rectify. PEFS: Prioriteit: Additional mitigations : Requester Name : KAJA MAIDEEN Phone : 44032213 27.03.2021 11:11:00 UTC Ashish Khataria (QRAKHB) pipe replaced.
90643699 | 2021-03-30 | A081-1SB220N2 | Poor lighting around 1P-6142 | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10373779 | 700002356603 | ABB MALAYSIA | Electrical | 35.06 | 4.1 | 4.1 | Internal failure / short | Internal failure / short- | Lamps | Repair / correct | 19.03.2021 21:39:27 UTC Ketan Pathak (QRKPA2) Clear description of the problem. Many light fixtures are not working around 1P-6142 and GOX B/L I/V and entrance of AC pipe rack west side PEFS: Prioriteit: X Scaffold Requester Name : Ketan Pathak Phone : 44032313 30.03.2021 12:48:27 UTC Sudheer Kumar Pendurthi (QRSPE6) Found breaker tripped condition (1SB220N2-Q42 / CKT-24, 1SB220N2-Q32 / CKT-12, 1SB220N2-Q19 / CKT-01)reset OK now, under observation
90643709 | 2021-03-27 | A081-0S0123A | 0S-0123A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373658 | 700002201322 | DKME | Integrity | 16656.1 | 29 | 49 |  |  |  |  | 18.03.2021 07:43:29 UTC Sivakumar Manokaran (QRSMAA) 0S-0123A filter element to be replaced with new one. due to filter DP high
90643766 | 2021-03-22 | A081-0A8350 | HMI ISSUE IN BSTD | MX04 | M_X_X | Schedule Breaker | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10373832 | 700002779390 |  | Integrity | 0 | 0 | 0 | Other - please specify in text field | Other - please specify in text field-OPER FGROUP WAS UNAUTHORISED | Software | Other - please specify in text field | 21.03.2021 04:32:01 UTC Shinde Villas (QRSVI3) Clear description of the problem. BSTD HMI IS NOT ACCEPTING PASSWORD CONTINUELY ASKING PASSWORD.WE CAN NOT START UNIT, NEED URGENT INSTRUMENT SUPPORT. PEFS: Prioriteit: Additional mitigations : X JHA needed Requester Name : VILAS SHINDE Phone : 44032215
90643865 | 2021-03-24 | A081-1F5111 | 1F5111,W-B2 FLAPPER WINDOW GLASS BRKN** | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10373873 | 700002348459 | KTI | Integrity | 0 | 0 | 18 |  |  |  |  | 22.03.2021 01:02:07 UTC Patrick Tirso Alegria (QRPAL0) Clear description of the problem. During flapper observation window temperature survey, W-B2 (west window top PF, facing GTL), found broken/crack. Glass to be replaced PEFS: Prioriteit: Additional mitigations : Requester Name : Patrick Alegria Phone : 6648-0081 (SMR IS Phone)
90644067 | 2021-05-05 | A081-0S0123A | 0S-0123A HIGH DP | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373937 | 700002201322 | DKME | Integrity | 1652.66 | 29 | 49
90644069 | 2021-05-01 | A081-0S0123B | 0S-0123B HIGH DP | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373938 | 700002200643 | DKME | Integrity | 236.37 | 29 | 49
90644071 | 2021-05-22 | A081-0S0143A | 0S-0143A HIGH DP | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373939 | 700002201324 | DKME | Integrity | 0 | 29 | 49
90644073 | 2021-05-18 | A081-0S0143B | 0S-0143B HIGH DP | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373940 | 700002202402 | DKME | Integrity | 165.67 | 29 | 49
90644074 | 2021-05-03 | A081-0S0163A | 0S-0163A HIGH DP | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373942 | 700002200042 | DKME | Integrity | 236.41 | 29 | 49
90644076 | 2021-05-15 | A081-0S0163B | 0S-0163B HIGH DP-> | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10373943 | 700002200043 | DKME | Integrity | 546.03 | 29 | 49
90644204 | 2021-03-29 | A081-0A8350 | BSTD TRIP&ARCM HAVING ELEC FAUL 0CP230E1 | MX04 | M_X_X | Schedule Breaker | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10374037 | 700002779390 |  | Integrity | 386.25 | 16 | 0 | Human Error | Human Error-Festoon Pendant struck | Other - please specify in text field | Fix / Repair | 24.03.2021 02:03:09 UTC "Jeyakaran, " Cifas (QRCJE0) Clear description of the problem. BSTD UNIT RIPPED - TO CHECK AND RECTIFY Last 3 days 4 times tripped - to check why it got tripped and rectify PEFS: Prioriteit: Additional mitigations : Requester Name : CIFAS JEYAKARAN Phone : 44032215 24.03.2021 05:22:58 UTC Raju Sutham (QRRSU3) ARCM having electrical issue, need to rectify by electrical. 0CP 230 E1 CONTROL CIRCUIT.BSTD UNIT RIPPED - TO CHECK AND RECTIFY Last 3 days 4 times tripped - to check why it got tripped and rectify 01.04.2021 15:03:17 UTC Joly Poulose (QRJVI4) carried out troubleshooting of moving system and test run with operator, system is working normal, while moving the system, pendent cable stretch and 9cable of Festoon Pendant disconnected from cable lugs. all cable terminated back and deisolated.
90644298 | 2021-03-27 | A081-0S0143B | 0S-0143B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10374104 | 700002202402 | DKME | Integrity | 305.91 | 29 | 49 |  |  |  |  | 24.03.2021 14:09:43 UTC Sivakumar Manokaran (QRSMAA) 0S-0143B filter DP high need to repalce the fitler element
90644560 | 2021-04-24 | A081-294XA-50200-S | 294XA50200,EHT COMMON FAIL,2ET-LPU-HD03* | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10374294 | 700002607282 |  | Instrumentation | 4393.31 | 28 | 58.1 | Internal failure / short | Internal failure / short-ECM module failure | Electronic / control board | Replace
90645168 | 2021-04-24 | A081-1SB220N2 | poor lighting near SGP finger-2 | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10374109 | 700002356603 | ABB MALAYSIA | Electrical | 438.13 | 6 | 6 | end of life | end of life- | Lamps | Replace
90645451 | 2021-05-17 | A081-0S0123A | 0S-0123A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10374808 | 700002201322 | DKME | Integrity | 7245.56 | 27 | 47
90645452 | 2021-05-15 | A081-0S0123B | 0S-0123B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10374809 | 700002200643 | DKME | Integrity | 7253.09 | 27 | 47
90645453 | 2021-05-26 | A081-0S0143A | 0S-0143A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10374810 | 700002201324 | DKME | Integrity | 3969.3 | 27 | 47
90645454 | 2021-05-26 | A081-0S0143B | 0S-0143B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10374811 | 700002202402 | DKME | Integrity | 7015.2 | 27 | 47
90645456 | 2021-05-12 | A081-0S0163A | 0S-0163A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10374812 | 700002200042 | DKME | Integrity | 7291.44 | 27 | 47
90645457 | 2021-05-01 | A081-0S0163B | 0S-0163B HC FILTER REPLACEMENT- PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10374813 | 700002200043 | DKME | Integrity | 1342.34 | 27 | 47
90645773 | 2021-04-10 | A081-0S0143A | 0S-0143A FILTER DP HIGH-SCE | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10375065 | 700002201324 | DKME | Integrity | 334.8 | 27 | 47
90646296 | 2021-04-19 | A081-1S0241 | 1S-0241 FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10375399 | 700002354895 | JFC CORPORATION | Integrity | 1512.56 | 29 | 67
90646718 | 2021-04-18 | A081-2A8324 | DAF-2 DAMAGE WHEEL TO BE REPLACED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10375687 | 700002297332 |  | Rotating | 510.42 | 6 | 0 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90647299 | 2021-04-29 | A081-2SB210N2 | 2V-3026 Lighting around Not Working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10375778 | 700002373562 | ABB MALAYSIA | Electrical | 17.52 | 2 | 2 | end of life | end of life- | Lamps | Check/ Inspect/ Test
90647671 | 2021-04-24 | A081-2A8324 | 2A 8324 SCRAPPER SMALL WHEEL DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10376059 | 700002297332 |  | Rotating | 67.69 | 0 | 86 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90647955 | 2021-05-06 | A081-1F5111 | 1F5111,WINDOW FLAPPER,WE1,HIGH TEMP | MX04 | M_FUR_X | UserDefined Priority | 0 |  | SMR FURNACE | CM | LPU |  | 700002348459 | KTI | Integrity | 0 | 0 | 0
90647975 | 2021-06-07 | A081-0P2021 | ASU7 ACC CLEANING PUMP FERRULE DAMAGE | MX04 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10373462 | 700002199414 | PRATISSOLI | Rotating | 1126.98 | 7 | 7 |  |  |  |  | 16.03.2021 07:35:49 UTC Maideen Kaja (QRMKA9) Clear description of the problem. ASU-7 ACC cleaning pump recycle flex ferrule fitting is observed in sheared off condition. Need to be fixed for ACC cleaning. PEFS: Prioriteit: Additional mitigations : Requester Name : KAJA Phone : 44032213 12.06.2021 04:50:02 UTC Akhilesh Nair (QRANAB) Below activities done 1. Ensure pump is not connected to plant supply - confirm with FO 2. Remove the damaged sheared off fitting. Cut using hacksaw if required. 3. Provide new ferrule fitting on the recycle flex. Refer attached image. 4. Perform proper housekeeping.
90648559 | 2021-05-13 | A081-1SB220N2 | PMFLT_U11200 36/ 18W LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10376621 | 700002356603 | ABB MALAYSIA | Electrical | 5134.24 | 64 | 108 | end of life | end of life- | Lamps | Replace
90648567 | 2021-08-17 | A081-1SB220N2 | PMFLT_AC_ AREA 36W LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10376624 | 700002356603 | ABB MALAYSIA | Electrical | 4676.68 | 74 | 80 | end of life | end of life- | Lamps | Replace | 26.04.2021 08:00:05 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. DURING LIGHTING VISUAL INSPECTION 1SB220N2 (90584665) FOUND 56 LIGHTING FIXTURE 36W NOT WORKING IN MAIN PIPE RACK AREA, NEED TO REPLACE LAMPS 36W - 112 NOS LAMP REQUIRED. 36W DIFFUSE NEED TO REPLACE 10 NOS. SEE ATTACHED QAQC NOTE- MOBILE SCAFFOLDING REQUIRED (FOR PIPE RACK) PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X JHA needed Requester Name : SHYAM TIWARI Phone : 70482757
90648692 | 2021-05-22 | A081-2SB200N2 | BUSTED,TUBE LIGHTS,GTL2,HPS 2ndSTAGE,CCO | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10376799 | 700002373557 | ABB MALAYSIA | Electrical | 165.56 | 10 | 186 | end of life | end of life- | Lamps | Replace
90648701 | 2021-05-18 | A081-0S0163B | 0S-0163B FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10376736 | 700002200043 | DKME | Integrity | 0 | 27 | 47
90648702 | 2021-05-17 | A081-0S0123B | 0s-0123B fitler element to be repaced | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10376737 | 700002200643 | DKME | Integrity | 69.72 | 29 | 49
90649176 | 2021-05-16 | A081-0P2021 | ACC cleaning pump 0P-2021 suction hose | MX04 | M_PUM_RECI | Routine Wrk Lvl 3 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10376843 | 700002199414 | PRATISSOLI | Rotating | 1043.64 | 5 | 5
90649184 | 2021-01-02 | A081-1F5111 | 1F5111,WINDOW FLAPPER, WK2 STUCK UP | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10377076 | 700002348459 | KTI | Integrity | 91.93 | 10 | 10 | Fouling | Fouling-Flapper struck | Other - please specify in text field | Fix / Repair
90649204 | 2021-05-03 | A081-1A8324 | DAF-1 SCRAPER SMALL WHEEL DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10377071 | 700002348718 |  | Rotating | 345.18 | 8 | 62 | Other - please specify in text field | Other - please specify in text field-damage wheel | Other - please specify in text field | Replace
90649330 | 2021-05-15 | A081-1SB210N2 | Lighting Not working 1R-3023 Top | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10377228 | 700002352082 | ABB MALAYSIA | Electrical | 7.27 | 4 | 10 | end of life | end of life- | Lamps
90650018 | 2021-01-02 | A081-1F5111 | 1F5111,WINDOW FLAPPER, W-F1 STUCK UP | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10377683 | 700002348459 | KTI | Integrity | 0 | 10 | 10 | Fouling | Fouling- | Other - please specify in text field | Fix / Repair
90650022 | 2021-05-08 | A081-0S0163B | 0S-0163B FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10377694 | 700002200043 | DKME | Integrity | 0 | 27 | 47
90650023 | 2021-05-17 | A081-2SB210N2 | 2C-3401 lighting not working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10377682 | 700002373562 | ABB MALAYSIA | Electrical | 365.26 | 10 | 10 | end of life | end of life- | Lamps | Replace
90650167 | 2021-05-11 | A081-0P2021 | OP-2021 tripped on lube pressure low | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10377672 | 700002199414 | PRATISSOLI | Rotating | 215.07 | 8 | 0 | Power / other utility failure | Power / other utility failure-Transmitter problem | Instrumentation | Fix / Repair
90650604 | 2021-05-18 | A081-0S0123A | 0S-0123A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10378010 | 700002201322 | DKME | Integrity | 7207.53 | 27 | 47
90650605 | 2021-05-20 | A081-0S0163B | 0S-0163B FILTER need to replacement | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10378092 | 700002200043 | DKME | Integrity | 3686.82 | 27 | 47
90650606 | 2021-05-17 | A081-0S0163A | 0S-0163A FILTER need to replacement | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10378094 | 700002200042 | DKME | Integrity | 5688.71 | 27 | 47
90650607 | 2021-05-19 | A081-0S0123B | 0S-0123B filter replacement during piggi | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10378093 | 700002200643 | DKME | Integrity | 2184.34 | 29 | 49
90650648 | 2021-05-16 | A081-2A8324 | DAF 2 SCRAPER SMALL WHEEL LINER DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10378143 | 700002297332 |  | Rotating | 0 | 12 | 0 | Normal Wear | Normal Wear- | Rotating element | Replace
90650785 | 2021-05-24 | A081-0X0104 | 0X-0104 screw conveyor sight glass broke | MX04 | M_PAC_CON2 | Schedule Breaker | 0 |  | SCREW CONVEYOR | CM | FGP | 10378172 | 700002206193 |  | Electrical | 6624.8 | 65 | 136 | Fouling | Fouling- | drive system | Replace
90651068 | 2021-06-17 | A081-2SB210N2 | PMFLT_2SB210N2 RCD/MCB CHECK/REPLACEMEN | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10378330 | 700002373562 | ABB MALAYSIA | Electrical | 131.42 | 10.1 | 10.1 | Internal failure / short | Internal failure / short-ELR NOT TRIPPING ON 30mA SETTING | Relay / contactor | Check/ Inspect/ Test | 17.05.2021 12:12:10 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. WHILE EXECUTING RCD TESTING UNDER WO 90610891 OBSERVED SOME RCD OF 2SB210N2 NOT TRIPPED. NEED TO DO RETEST AND IF FOUND FAULTY NEED TO REPLACE. CHECK RCD OF FOLLOWING CKTS. CKT 32-L1, CKT 32-L3, CKT 33-L1, CKT 33-L3, CKT 34-L1, CKT 34-L3, CKT 35-L2 PEFS: Prioriteit: Additional mitigations : Electrical tasks: X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198
90651072 | 2021-05-19 | A081-1A8324 | DAF1 SMALL WHEEL DAMAGED TO BE REPLACED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10378359 | 700002348718 |  | Rotating | 473.65 | 6 | 0 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90651091 | 2021-05-23 | A081-0S0123A | 0S-123 A HC FILTERE REPLACEMENT. | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10378367 | 700002201322 | DKME | Integrity | 196.17 | 29 | 49
90651092 | 2021-06-01 | A081-0S0123B | 0S-123 B HC FILTER REPLACEMNT - PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10378368 | 700002200643 | DKME | Integrity | 141.06 | 29 | 49 |  |  |  |  | 18.05.2021 05:43:35 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-123 B HC FILTER REPLACEMENT TO BE DONE BASED ON DEMAND.
90651093 | 2021-05-19 | A081-0S0163A | 0S-163 A HC FILTER REPLACEMENT. | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10378370 | 700002200042 | DKME | Integrity | 282.01 | 27 | 47
90651094 | 2021-06-12 | A081-0S0163B | 0S-163 B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10378371 | 700002200043 | DKME | Integrity | 10098.55 | 27 | 47 |  |  |  |  | 18.05.2021 05:48:21 UTC Prabu Sankar Govindasamy Munusamy (QRPGO2) 0S-163 B HC FILTER NEED TO BE REPLACEED BASED ON DEMAND.
90651376 | 2021-06-19 | A081-1SB220N2 | Poor lightings 1F-1121 East side | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10378438 | 700002356603 | ABB MALAYSIA | Electrical | 458.15 | 24 | 16 | end of life | end of life- | Lamps | Replace | 19.05.2021 01:01:08 UTC Saravanakumar Mani (QRSMA4) Clear description of the problem. Lightings not working near 1V-1120 (1LFN220N240L325) and flood light for fuel skid(LT) PEFS: Prioriteit: Requester Name : Saravana Phone : 44032313
90651379 | 2021-06-19 | A081-1SB210N2 | AB_REACTOR TOPSIDE_400W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10378390 | 700002352082 | ABB MALAYSIA | Electrical | 602.23 | 27 | 43 | end of life | end of life- | Lamps | Replace | 18.05.2021 08:12:00 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. DURING TROUBLESHOOTING OF FAULTY LAMPS UNDER WO 90649330 FOUND AROUND 7 HIGH BAY 400W LIGHTS NOT GLOWING ON THE TOP OF THE REACTOR. NEED TO REPLACE. CRAINE ISOLATION REQUIRED FOR ERECTING SCAFFOLDING ON THE TOP OF THE CRAINE FOR ACCESS FOR TROUBLESHOOTING. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198
90653345 | 2021-06-08 | A081-1SB220N2 | Poor lighting near 1R-1116 | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10378604 | 700002356603 | ABB MALAYSIA | Electrical | 337.24 | 32.1 | 34.1 | end of life | end of life- | Lamps |  | 20.05.2021 06:46:13 UTC Dharmendrakumar Suthar (QRDSU0) Clear description of the problem. POOR LIGHTING FOUND NEAR 1R-1116 , Particularly near SEC-B ground floor and 3rd floor. Need to be followed. PEFS: T-13.370.353 Prioriteit: X WPS/ Work instruction needed X Use moveable platform or man lift Electrical tasks: Requester Name : DHARMENDRA SUTHAR Phone : 44032313
90653532 | 2021-06-07 | A081-1A8324 | DAF1 SMALL WHEEL ALIGNMEN CHECKTO BE | MX04 | M_ROT_X | Routine Wrk Lvl 2 | 0 |  | DAF Scraper Assembly | CM | ETP | 10378613 | 700002348718 |  | Rotating | 0 | 0 | 0 |  |  |  |  | 20.05.2021 08:14:10 UTC Arunbhai Patel (QRAPA0) Clear description of the problem DAF1 SMALL WHEEL ALIGNMENT CHECK NEW MODIFY SMALL WHEEL FRAME INSTALL Name ARUNBHAI PATEL Phone number 44032709 What is the problem? Beacon not working What work is required? (Troubleshoot/Repair/replace) Trouble shoot What mitigations has been taken? NA Has a photo/sketch/document been provided? NO Is the location marked with a Maintenance tag? Yes Special requirements for the repair: Is material required for the repair? Yes Is a specialist/vendor/manpower required? No Is special tool/equipment required? No Specify the work location: (e.g. LQ Level 1) A081-1A8324
90653533 | 2021-06-02 | A081-2A8324 | T2 DAF SMALL WHEEL ADJUSTMENT | MX04 | M_ROT_X | Routine Wrk Lvl 2 | 0 |  | DAF Scraper Assembly | CM | ETP | 10378622 | 700002297332 |  | Rotating | 134.49 | 19 | 19 |  |  |  |  | 20.05.2021 09:14:52 UTC Pareshkumar Kanubhai Vyas (QRPVY0) Clear description of the problem. PHASE 2 DAF SKIMMER SMALL WHEEL NEED TO BE ADJUSTED AS WHILE RUNNING MAKING NOISE,C <(>&<)> D SMALL WHEEL MARKED ON LOCATION, FOR PROACTIVE MEASURE NEED TO ALIGN THE BOGIE BRACKET PEFS: T-4.118.867 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. NO X Scaffold Electrical tasks: X JHA needed Requester Name : VYAS PARESHKUMAR KANUBHAI Phone : 44032717 05.06.2021 07:40:42 UTC Sunil Rajput (QRSRBF) Wheel alignment done as per PRS.
90653801 | 2022-01-25 | A081-294XA-50200-S | 2ET-LDF-05(243RV-10001)EHT ALM*TO BE REP | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10379022 | 700002607282 |  | Instrumentation | 9301.21 | 58 | 151.6 | Premature failure | Premature failure- | Thermostat / Temp. relay | Replace
90653846 | 2021-06-02 | A081-0S0143B | 0S-0143B filter DP high - PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10379045 | 700002202402 | DKME | Integrity | 6584.5 | 29 | 49 |  |  |  |  | 24.05.2021 21:13:04 UTC Sivakumar Manokaran (QRSMAA) 0S-0143B filter element DP is high need to replace the filter elements.
90653847 | 2021-05-29 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10379040 | 700002201322 | DKME | Integrity | 10392.67 | 29 | 49
90653848 | 2022-06-04 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10379041 | 700002200643 | DKME | Integrity | 10717.85 | 29 | 49
90653849 | 2021-06-24 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10379042 | 700002201324 | DKME | Integrity | 10755.32 | 27 | 47 |  |  |  |  | 24.05.2021 18:16:22 UTC Suresh Babu Narayanan (QRSNA7) 0S-0143A filter element replacement for the Pearl-1 pigging purpose.
90653850 | 2021-07-15 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10379043 | 700002202402 | DKME | Integrity | 4217.66 | 49 | 49
90653995 | 2021-05-26 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10379149 | 700002200643 | DKME | Integrity | 0 | 29 | 49
90653996 | 2021-05-27 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10379150 | 700002201324 | DKME | Integrity | 0 | 0 | 0
90654379 | 2021-05-29 | A081-0S0143B | 0S-0143B Filter Elements Replacement | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380022 | 700002202402 | DKME | Integrity | 213.7 | 29 | 49
90654382 | 2021-05-29 | A081-0S0163B | 0S-0163B FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380003 | 700002200043 | DKME | Integrity | 17428.59 | 30 | 49
90654396 | 2021-06-22 | A081-2SB210N2 | 2V-3421 Lighting not working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10380018 | 700002373562 | ABB MALAYSIA | Electrical | 245.8 | 24 | 16 | end of life | end of life- | Lamps | Replace | 30.05.2021 00:00:34 UTC Khairul Anuwa Muda (QRKBI0) lear description of the problem. During field check activities, found 2V-3421 lighting not working .lighting list attached. PEFS: t-4.002.549 Prioriteit: Additional mitigations : Requester Name : Khairul.BinMuda Phone : 2311 08.06.2021 08:47:25 UTC Mohammad Alam (QRMANR) MATERIAL RESERVED THROUGH WO 90651376
90654533 | 2022-05-17 | A081-0S0123B | 0s-0123B fitler element to be repaced | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380055 | 700002200643 | DKME | Integrity | 3458.68 | 48 | 49
90654534 | 2022-05-30 | A081-0S0123A | 0s-0123A filter element to be repalced | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380056 | 700002201322 | DKME | Integrity | 3592.21 | 25 | 49
90654535 | 2022-03-26 | A081-0S0143A | MTASTR 0s143A filter element replacement | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380057 | 700002201324 | DKME | Integrity | 17680.52 | 21 | 49
90654536 | 2021-11-04 | A081-0S0143B | 0S-0143B FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380058 | 700002202402 | DKME | Integrity | 445.92 | 49 | 49
90654538 | 2021-08-28 | A081-0S0163B | 0S-0163B FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380059 | 700002200043 | DKME | Integrity | 656.23 | 49 | 49 |  |  |  |  | 30.05.2021 08:00:16 UTC Sivakumar Manokaran (QRSMAA) 0s-0163B filter element to be repalced
90654540 | 2021-08-28 | A081-0S0163A | 0S-0163A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380060 | 700002200042 | DKME | Integrity | 408.47 | 49 | 49 |  |  |  |  | 30.05.2021 08:01:35 UTC Sivakumar Manokaran (QRSMAA) 0s-0163A filter element to be replaced
90654541 | 2022-06-20 | A081-0S0123A | 0s-0123A filter element to be repalced | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380069 | 700002201322 | DKME | Integrity | 3407.47 | 49 | 49
90654542 | 2022-06-06 | A081-0S0123B | 0s-0123B fitler element to be repaced | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380070 | 700002200643 | DKME | Integrity | 3410.53 | 29 | 49
90654543 | 2021-07-10 | A081-0S0163A | 0S-0163A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380072 | 700002200042 | DKME | Integrity | 0 | 49 | 49
90654949 | 2021-06-06 | A081-0X0104 | 0x-0104 screw conveyer cleaning required | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10380208 | 700002206193 |  | Electrical | 0 | 6 | 10 | Fouling | Fouling-Proactive cleaning and inspection | drive system | Cleaned | 31.05.2021 21:08:37 UTC Sivakumar Manokaran (QRSMAA) DEFECT FOUND: 0X-0104 EQUIPMENT FUNCTION: DRM filter SUGGESTED FIX REQUIRED: Mechanical MANNING, MATERIAL AND TOOLS REQUIRED: yes LOCATION/ACCESS ISSUES: No HEALTH, SAFETY <(>&<)> ENVIRONMENTAL CONSIDERATIONS: Nil REASONING BEHIND CMPT RANKING: 1B ANY SHUTDOWN REQUIRED/ISOLATION: NO OTHER INFO/ATTACHMENTS (Drawings/Photos/Sketches: After batch preparation Screw conveyer to be cleaned
90655163 | 2021-06-02 | A081-0S0163A | 0S163A filter element to be replaced-PRD | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380487 | 700002200042 | DKME | Integrity | 437.64 | 29 | 49 |  |  |  |  | 02.06.2021 00:11:00 UTC Sivakumar Manokaran (QRSMAA) 0S-0163A filter elements DP high need to repalce the filter elements.
90655637 | 2021-06-05 | A081-0S0163A | 0S-0163A filter elements to be replaced | MX09 |  | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380879 |  |  |  | 15142.13 | 27 | 47 |  |  |  |  | 06.06.2021 04:23:32 UTC Sivakumar Manokaran (QRSMAA) 0S-0163B filter elements DP high need tor epalce the filter elements
90655638 | 2021-06-05 | A081-0S0143B | 0S-0143B FILTER DP HIGH | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10380878 | 700002202402 | DKME | Integrity | 196.05 | 27 | 47 |  |  |  |  | 06.06.2021 04:18:03 UTC Sivakumar Manokaran (QRSMAA) 0S-0143B filter DP high need to repalce the filter elements
90655694 | 2021-06-06 | A081-1A8324 | TR1 DAF SMALL WHEEL DAMAGED CONDITION | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10380867 | 700002348718 |  | Rotating | 592.75 | 54 | 54 | Normal Wear | Normal Wear-small wheel damage | Rotating element | Replace | 05.06.2021 21:56:02 UTC Mubassar Ahmed (QRMAH5) Clear description of the problem. Train 1 DAF Scrapper small wheel outer rubber lining peeled off. Photo attached.(One wheel only)) PEFS: : Requester Name : MUBASSAR AHMED Phone : 06.06.2021 00:46:03 UTC Vaghasiya Bhimjibhar (QRVBH2) EACH ARM OF SCRAPPER BRIDGE ONE WHEEL DAMAGED. SO IN BOTH ARM TOTAL TWO SET OF WHEEL TO BE REPLACED. 08.06.2021 04:58:03 UTC Pareshkumar Kanubhai Vyas (QRPVY0) two set of wheel replaced which are marked on location. A <(>&<)> C are replaced. mechanical job is completed.
90655695 | 2021-06-08 | A081-2A8324 | TR2 DAF SCRAPPER WHEEL DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10380868 | 700002297332 |  | Rotating | 579.35 | 8 | 0 | Normal Wear | Normal Wear- | Rotating element | Replace | 05.06.2021 22:12:15 UTC Mubassar Ahmed (QRMAH5) Clear description of the problem. DAF 2 SCRAPPER SMALL WHEEL OUTER RUBBER LINNING PEELED OFF (02 wheels). photo is attached. PEFS: Requester Name : MUBASSAR AHMED Phone : 06.06.2021 00:53:34 UTC Vaghasiya Bhimjibhar (QRVBH2) DOWN STREAM OF MOTOR SIDE SCRAPPER BRIDGE ARM TOTAL THREE WHEELS ARE DAMAGED.SO TWO SET OF WHEEL TO BE REPLACED. 09.06.2021 04:09:40 UTC Pareshkumar Kanubhai Vyas (QRPVY0) Three set of wheel replaced with new one, a, B <(>&<)> C were replaced with new one.
90655776 | 2021-06-08 | A081-0X0104 | Screw conveyer cleaning requried- 0X-104 | MX04 | M_PAC_CON2 | Schedule Breaker | 0 |  | SCREW CONVEYOR | CM | FGP | 10380897 | 700002206193 |  | Electrical | 83.22 | 6 | 10 | Preventive Maintenance Work | Preventive Maintenance Work-PROACTIVE CLENAING AS PART OF BATCH PREP | drive system | Cleaned | 06.06.2021 09:31:40 UTC Sethuraj Nagaraj (QRNSE0) DEFECT FOUND: 0X-0104 EQUIPMENT FUNCTION: DRM filter SUGGESTED FIX REQUIRED: conveyer cleaning to be done. MANNING, MATERIAL AND TOOLS REQUIRED: yes, As per cleaning requriement. LOCATION/ACCESS ISSUES: 1A1 Slug catcher, NO Access issue. HEALTH, SAFETY & ENVIRONMENTAL CONSIDERATIONS: Hot weather REASONING BEHIND CMPT RANKING: 1B ANY SHUTDOWN REQUIRED/ISOLATION: Electrical isolation requried OTHER INFO/ATTACHMENTS (Drawings/Photos/Sketches: Nil
90655796 | 2021-06-14 | A081-1F5111 | 1F5111,BNR UPGRADE 5 NOS.;MOC | MX09 | M_FUR_X | Routine Wrk LvL 5 | 0 |  | SMR FURNACE | CM | LPU | 10380916 | 700002348459 | KTI | Integrity | 4110.59 | 346 | 393
90656295 | 2021-06-08 | A081-0S0143A | 0S-0143-A filter element repalcement-PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10381150 | 700002201324 | DKME | Integrity | 226.11 | 29 | 49 |  |  |  |  | 09.06.2021 01:15:04 UTC Suresh Babu Narayanan (QRSNA7) 0S-0143-A filter element to be replaced.
90656453 | 2021-06-20 | A081-0X0104 | 0x-0104 screw conveyer cleaning required | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10381220 | 700002206193 |  | Electrical | 166.45 | 6 | 10 | Fouling | Fouling- | drive system | Cleaned | 09.06.2021 22:26:36 UTC Sivakumar Manokaran (QRSMAA) Dr.M filter New batch prepared on 10/6/2021, screw conveyer to be cleaned.
90656494 | 2021-06-12 | A081-1S0241 | 1S-0241 FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10381252 | 700002354895 | JFC CORPORATION | Integrity | 1261.24 | 29 | 67 |  |  |  |  | 10.06.2021 07:02:32 UTC Youcef Kenef (QRYKE0) Clear description of the problem. 1S-0241 Filter DP increased Filter elements need to be replaced. PEFS: T-13.370.089 Prioriteit: X WPS/ Work instruction needed X Scaffold Requester Name : Youcef Phone : 44032111
90656744 | 2021-09-13 | A081-1SB220N2 | 1R-1116 AREA LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10381459 | 700002356603 | ABB MALAYSIA | Electrical | 1021.99 | 45 | 57 | end of life | end of life- | Lamps | Replace
90657132 | 2021-08-01 | A081-1S0241 | 1S-0241 FILTER ELEMENT TO BE REPLACED> | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10381700 | 700002354895 | JFC CORPORATION | Integrity | 1470.04 | 67 | 67 |  |  |  |  | 15.06.2021 06:40:58 UTC Youcef Kenef (QRYKE0) Clear description of the problem. 1S-0241 Filter DP increased Filter elements need to be replaced ASI. PEFS: T-13.370.089 Prioriteit: X WPS/ Work instruction needed X Scaffold Requester Name : Youcef Phone : 44032111
90657208 | 2021-07-10 | A081-1SB220N2 | 1C-1211 / 1212 poor lighting | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10381753 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 16 | 16 | end of life | end of life- | Lamps | Replace
90657381 | 2021-06-28 | A081-FIRE HYDRANT | FH165 2.5" CAP STUCK,TR2 ;FIX** | MX04 |  | Routine Wrk Lvl 1 | 0 |  | FIRE HYDRANT | CM | UTL | 10381190 |  |  |  | 0 | 0 | 13
90657839 | 2021-06-28 | A081-2SB210N2 | 2SB210N2_CKT 32L1 RCD REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10382029 | 700002373562 | ABB MALAYSIA | Electrical | 148.95 | 12 | 12 | Internal failure / short | Internal failure / short- | Fuse / MCB | Replace | 19.06.2021 04:10:16 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. WHILE RETESTING OF RCD UNDER WO 906510668, FOUND THAT RCD OF CKT 32L1 PHASE IS FAULTY. NEED TO REPLACE. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X E-Disconnect X E-isolation Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198 19.06.2021 07:03:32 UTC Hareshkumar Chauhan (QRHCH2) Material Code-10663250 1nos. required
90657932 | 2022-06-18 | A081-2A8324 | RETA: DAF2 SCRAPPER BIG WHEEL LINING DAM | MX04 | M_ROT_X | Routine Wrk Lvl 4 | 0 |  | DAF Scraper Assembly | CM | ETP | 10379084 | 700002297332 |  | Rotating | 4155.04 | 118 | 136
90658151 | 2021-06-24 | A081-2A8324 | TR2 DAF SMALL WHEEL CONDITION BAD FO1 | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10382403 | 700002297332 |  | Rotating | 203.22 | 6 | 0 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace | 22.06.2021 10:29:03 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. TR2 DAF SMALL WHEEL (C) TOP LAYER PEELED OFF ,CONDITION IS GOING WORST.PHOTO ATTACHED.TO BE REPLACE ASAP. PEFS: Prioriteit: Additional mitigations : Requester Name : Raja.Ramasamy Phone : +97444032215 23.06.2021 10:29:17 UTC Arunbhai Patel (QRAPA0) Replaced new two small whell
90658343 | 2021-12-04 | A081-1SB220N2 | GTL-1_AC AREA 36W POOR LIGHTING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10382509 | 700002356603 | ABB MALAYSIA | Electrical | 2312.5 | 36 | 261 | end of life | end of life- | Lamps | Replace
90658365 | 2021-06-27 | A081-1A8324 | TR1 DAF SCUM BOARD CHAIN REMOVED FROM HO | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10382633 | 700002348718 |  | Rotating | 258.24 | 16 | 0 | Normal Wear | Normal Wear- | Other - please specify in text field | Fix / Repair | 24.06.2021 05:14:56 UTC Raja Ramasamy (QRRRA2) Clear description of the problem. DAF TR1 SCUM BOARD CHAIN HOOK REMOVED FROM ONE SIDE.NEED TO FIX IT ASAP.PHOTO ATTACHED. PEFS: Prioriteit: Additional mitigations : Requester Name : Raja.Ramasamy Phone : 44032215 24.06.2021 14:33:12 UTC Pareshkumar Kanubhai Vyas (QRPVY0) Scrapper latch was detached and which is atteded by providing the D shackles also tighten the d shackles pin thread. Trial run was taken found normal. mechanicaljob is completed.
90658597 | 2021-06-28 | A081-1A8324 | TR 1 DAF SMALL WHEEL DAMAGE | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10382793 | 700002348718 |  | Rotating | 203.22 | 8 | 86 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace | 26.06.2021 10:09:54 UTC Leo Miranda (QRLMI0) Clear description of the problem. DAF 1 SCRAPPER SMALL WHEEL NO:C FOUND DAMAGED NEED TO REPLACED.PICTURE IS ATTACHED. SCAFFOLDING ALREADY AVAILABLE. PEFS: T-4.118.864 Prioriteit: Additional mitigations : X WPS/ Work instruction needed Electrical tasks: X E-isolation Requester Name : RAJESH Phone : 2215 28.06.2021 03:58:25 UTC Arunbhai Patel (QRAPA0) Replaced two new small wheel
90658920 | 2021-07-18 | A081-2SB200N2 | Train2 HPS BA area lighting not working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10383238 | 700002373557 | ABB MALAYSIA | Electrical | 94.87 | 18 | 37 | end of life | end of life- | Lamps | Replace
90658972 | 2021-07-28 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10383230 | 700002200043 | DKME | Integrity | 421.63 | 38 | 47
90658973 | 2021-11-20 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10383229 | 700002200043 | DKME | Integrity | 0 | 26 | 47
90658974 | 2022-01-11 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10383228 | 700002200042 | DKME | Integrity | 3773.94 | 47 | 47
90658975 | 2021-08-22 | A081-0S0163A | 0S-0163A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10383227 | 700002200042 | DKME | Integrity | 92.95 | 47 | 47 |  |  |  |  | 27.06.2021 20:15:40 UTC Narendra Yesupogu (QRNYE0) Clear description of the problem. U-0100,String-3,0S-0163A filter elements to be replaced due to high DP PEFS: T-4.094.342 Prioriteit: Additional mitigations : X JHA needed Requester Name : Narendra.Yesupogu Phone : 44032115
90658979 | 2021-07-06 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10383226 | 700002202402 | DKME | Integrity | 0 | 47 | 47
90658980 | 2021-07-31 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10383225 | 700002202402 | DKME | Integrity | 408.36 | 38 | 47
90658981 | 2021-07-11 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10383224 | 700002201324 | DKME | Integrity | 0 | 37 | 47
90658984 | 2022-04-07 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10383221 | 700002200643 | DKME | Integrity | 5851.87 | 0 | 47
90658986 | 2022-03-23 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10383219 | 700002201322 | DKME | Integrity | 5603.59 | 0 | 47
90659106 | 2021-07-25 | A081-1SB220N2 | Poor lighting in Finger-2 & 3 | MX04 |  | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10383392 |  |  |  | 3652.28 | 72 | 40 | end of life | end of life- | Lamps | Replace
90659110 | 2021-07-13 | A081-1SB210N2 | POOR LIGHTING IN AB AREA | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10383397 | 700002352082 | ABB MALAYSIA | Electrical | 592.76 | 16 | 16 | end of life | end of life- | Lamps | Replace
90659114 | 2022-01-11 | A081-1F5111 | 1F5111,GRATING LOOSE ;NEAR H2-H3 BNR** | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10383338 | 700002348459 | KTI | Integrity | 141.69 | 8 | 8 | Poor installation | Poor installation-HUMAN ERROR | Furnace grating | Other - please specify in text field
90659287 | 2021-07-14 | A081-294XA-50200-S | 2SB400E9-Q19(HMU PSA 2)EHT ELR TRIP RECT | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10383455 | 700002607282 |  | Instrumentation | 129.96 | 16 | 16 | Leakage | Leakage- | Relay / contactor | Check/ Inspect/ Test
90660083 | 2021-07-06 | A081-1A8324 | DAF-1 SMALL WHEEL NO:B DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10383875 | 700002348718 |  | Rotating | 200.43 | 91 | 89 | Other - please specify in text field | Other - please specify in text field-damage whell | Other - please specify in text field | Replace
90660307 | 2021-07-14 | A081-0X0104 | 0X-0104 SCREW CONVEOY CLEANING REQUIRED | MX04 | M_PAC_CON2 | Schedule Breaker | 0 |  | SCREW CONVEYOR | CM | FGP | 10383963 | 700002206193 |  | Electrical | 5.84 | 6 | 10 | Fouling | Fouling- | drive system | Cleaned
90660453 | 2021-08-07 | A081-1SB220N2 | AC 1R-1141 AREA 36W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10384044 | 700002356603 | ABB MALAYSIA | Electrical | 655.2 | 8 | 89 | end of life | end of life- | Lamps | Replace | 06.07.2021 11:35:17 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. GTL-1 SGP AREA WEST SIDE OF 1R-1141 GROUND FLOOR TWO LAMPS NOT GLOWING. LIGHTING FIXTURE TAG NOS. AS FOLLOW 1LFN220N205L309 1LFN220N205L118 3 MTR SCAFFOLDING REQUIRED FOR EACH LAMP PEFS: T-4.013.355 Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198 27.07.2021 06:38:54 UTC Mohammad Alam (QRMANR) 36W LAMP TO BE REPLACE 4 NOS
90660455 | 2021-08-11 | A081-1SB220N2 | AC 1R-1142B AREA 36W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10384046 | 700002356603 | ABB MALAYSIA | Electrical | 275.89 | 12 | 89 | end of life | end of life- | Lamps | Replace | 06.07.2021 11:38:47 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. GTL-1 SGP AREA WEST SIDE OF 1R-1142B GROUND FLOOR TWO LAMPS NOT GLOWING. LIGHTING FIXTURE TAG NOS. AS FOLLOW 1LFN220N205L112 1LFN220N205L216 3 MTR SCAFFOLDING REQUIRED FOR EACH LAMP PEFS: T-4.013.355 Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198 27.07.2021 06:39:52 UTC Mohammad Alam (QRMANR) 36W LAMP TO BE REPLACE 4 NOS 27.07.2021 07:40:36 UTC Mohammad Alam (QRMANR) MATERIAL BOOKED THROUGH WO 90660453
90660458 | 2021-08-10 | A081-1SB220N2 | AC 1R-1132A/B AREA 36W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10384047 | 700002356603 | ABB MALAYSIA | Electrical | 96.34 | 8 | 89 | end of life | end of life- | Lamps | Replace | 06.07.2021 11:42:13 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. GTL-1 SGP AREA WEST SIDE OF 1R-1132A <(>&<)> B GROUND FLOOR TWO LAMPS NOT GLOWING. LIGHTING FIXTURE TAG NOS. AS FOLLOW 1LFN220N205L107 1LFN220N205L230 3 MTR SCAFFOLDING REQUIRED FOR EACH LAMP PEFS: T-4.013.140 Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198 06.07.2021 11:47:26 UTC Hareshkumar Chauhan (QRHCH2) 1LFN220N201L230-SECOND NO. TAG 27.07.2021 06:41:35 UTC Mohammad Alam (QRMANR) 36W LAMP TO BE REPLACE 4 NOS 27.07.2021 07:43:28 UTC Mohammad Alam (QRMANR) MATERIAL BOOKED THROUGH WO 90660453
90660459 | 2021-08-07 | A081-1SB220N2 | AC 1R-1131 AREA 36W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10384048 | 700002356603 | ABB MALAYSIA | Electrical | 324.37 | 6 | 89 | end of life | end of life- | Lamps | Replace | 06.07.2021 11:45:22 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. GTL-1 SGP AREA WEST SIDE OF 1R-1131 GROUND FLOOR TWO LAMPS NOT GLOWING. LIGHTING FIXTURE TAG NOS. AS FOLLOW 1LFN220N205L103 1LFN220N205L203 3 MTR SCAFFOLDING REQUIRED FOR EACH LAMP PEFS: T-4.013.140 Prioriteit: Additional mitigations : Electrical tasks: X E-isolation X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198 27.07.2021 07:45:22 UTC Mohammad Alam (QRMANR) MATERIAL BOOKED THROUGH WO 90660453
90660590 | 2021-07-15 | A081-0X0104 | 0X-0104 SCREW CONVEYOR CLEANING | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10384128 | 700002206193 |  | Electrical | 166.45 | 6 | 10 | Other - please specify in text field | Other - please specify in text field-cleaning | Other - please specify in text field | Cleaned
90660595 | 2021-07-18 | A081-1A8324 | TR1 DAF SCUM BOARD CHAIN REMOVED FROM ON | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10384163 | 700002348718 |  | Rotating | 0 | 0 | 18
90660781 | 2022-04-03 | A081-0S0143A | 0S-0143A FILTER DP HIGH NEED TO REPLACE | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10384655 | 700002201324 | DKME | Integrity | 3348.18 | 21 | 47
90660789 | 2022-05-16 | A081-0S0163A | 0S-0163A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10384201 | 700002200042 | DKME | Integrity | 3545.2 | 28 | 47
90660943 | 2021-07-12 | A081-0S0163A | 0S-0163A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10384850 | 700002200042 | DKME | Integrity | 408.47 | 47 | 47
90660944 | 2021-07-17 | A081-1A8324 | FS-TR-1 DAF SKIMMER PLATE CHAIN DETACHED | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10384707 | 700002348718 |  | Rotating | 0 | 4 | 4 | Other - please specify in text field | Other - please specify in text field-chain detached | Other - please specify in text field | Fix / Repair
90661212 | 2021-07-25 | A081-1A8324 | FS-DAF 1 SCUM BOARD L CLAMP CHAIN DETACH | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10384920 | 700002348718 |  | Rotating | 70.65 | 16 | 8 | Other - please specify in text field | Other - please specify in text field-chain detached | Other - please specify in text field | Fix / Repair
90661291 | 2021-07-17 | A081-1A8324 | AH13 BYRNE CABLE PROTECTOR DAMAGED | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10385000 | 700002348718 |  | Rotating | 162.43 | 8 | 4 | Other - please specify in text field | Other - please specify in text field-BECAUSE OF HEAVY TRUCK MOVMENT | Other - please specify in text field | Replace
90661655 | 2021-07-18 | A081-0S0143B | 0S-0143-B filter replacement | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10385221 | 700002202402 | DKME | Integrity | 0 | 0 | 0
90661656 | 2021-07-18 | A081-0S0163B | 0S-0163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10385222 | 700002200043 | DKME | Integrity | 0 | 0 | 0
90661691 | 2021-07-25 | A081-0X0104 | 0X-0104 SCREW CONVEOY CLEANING REQUIRED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10385245 | 700002206193 |  | Electrical | 83.23 | 9 | 13 | Preventive Maintenance Work | Preventive Maintenance Work- | Rotating element | Cleaned
90661704 | 2021-07-26 | A081-0X0104 | 0XM-0104 motor internal fault trip | MX04 | E_MOT_LV | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10385208 | 700002203439 | DRM LOHER | Electrical | 111.66 | 8 | 8 | Overload | Overload-TOL Protection was active | Other - please specify in text field | Check/ Inspect/ Test
90661843 | 2021-12-25 | A081-1SB210N2 | AB_FINFAN TOP PLATFORM LAMP BUSTED | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10385385 | 700002352082 | ABB MALAYSIA | Electrical | 11010.63 | 99 | 81 | end of life | end of life- | Lamps
90661867 | 2021-07-27 | A081-1A8324 | TR1 DAF SCUM BOARD CHAIN DETACHED | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10385420 | 700002348718 |  | Rotating | 0 | 6 | 6 | Other - please specify in text field | Other - please specify in text field-chain detached | Other - please specify in text field | Fix / Repair
90661988 | 2022-02-07 | A081-2SB200N2 | BA_2LFN200N205L315 LIGHT FIXTURE FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10385472 | 700002373557 | ABB MALAYSIA | Electrical | 403.86 | 8 | 20 | end of life | end of life- | Lighting Fixture | Replace
90662166 | 2021-07-29 | A081-2A8324 | TR-2 DAF SMALL WHEEL-C DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10385587 | 700002297332 |  | Rotating | 200.41 | 0 | 0 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90662179 | 2021-08-25 | A081-1SB210N2 | AB_1LFN210N219L214 36W LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10385586 | 700002352082 | ABB MALAYSIA | Electrical | 126.97 | 6 | 37 | end of life | end of life- | Lamps | Replace | 20.07.2021 19:29:02 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. GTL-1 AB AREA 1E-3041 12M ELEVATION EAST SIDE OF EXCHANGER 1E-3041A/B, 1LFN210N219L214 36W LIGHT NOT WORKING. NEED TO CHECK <(>&<)> REPLACE THE FAULTY LAMPS. SCAFFOLDING REQUIRED 3-4 MTR. APPROX. FOR LOCATION REFER ATTACHED LIGHTING LAYOUT. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198
90662180 | 2021-08-28 | A081-1SB210N2 | AB_1LFN210N219L112 36W LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10385590 | 700002352082 | ABB MALAYSIA | Electrical | 55.35 | 2 | 29 | end of life | end of life- | Lamps | Replace | 20.07.2021 20:21:04 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. GTL-1 AB AREA 1E-3041 12M ELEVATION EAST SIDE OF EXCHANGER 1E-3041C/D, 1LFN210N219L112 36W LIGHT NOT WORKING. NEED TO CHECK <(>&<)> REPLACE THE FAULTY LAMPS. SCAFFOLDING REQUIRED 3-4 MTR. APPROX. FOR LOCATION REFER ATTACHED LIGHTING LAYOUT. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198 04.08.2021 12:57:46 UTC Mohammad Alam (QRMANR) MATERIAL RESERVED THROUGH WO 90662179
90662183 | 2021-08-28 | A081-1SB210N2 | AB_1LFN210N219L213 36W LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10385591 | 700002352082 | ABB MALAYSIA | Electrical | 138.45 | 4 | 33 | end of life | end of life- | Lamps | Replace | 20.07.2021 20:29:24 UTC Hareshkumar Chauhan (QRHCH2) lear description of the problem. GTL-1 AB AREA 1E-3041 12M ELEVATION NORTH SIDE OF EXCHANGER 1E-3041C/D, 1LFN210N219L213 36W LIGHT NOT WORKING. NEED TO CHECK <(>&<)> REPLACE THE FAULTY LAMPS. SCAFFOLDING REQUIRED 3-4 MTR. APPROX. FOR LOCATION REFER ATTACHED LIGHTING LAYOUT. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198 04.08.2021 12:57:59 UTC Mohammad Alam (QRMANR) MATERIAL RESERVED THROUGH WO 90662179
90662184 | 2021-08-28 | A081-1SB210N2 | AB_1LFN210N219L215 36W LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10385592 | 700002352082 | ABB MALAYSIA | Electrical | 48.58 | 4 | 33 | end of life | end of life- | Lamps | Replace | 20.07.2021 20:42:18 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. GTL-1 AB AREA 1E-3041 12M ELEVATION WEST SIDE OF EXCHANGER 1E-3041A/B, 1LFN210N219L215 36W LIGHT NOT WORKING. NEED TO CHECK <(>&<)> REPLACE THE FAULTY LAMPS. SCAFFOLDING REQUIRED 3-4 MTR. APPROX. FOR LOCATION REFER ATTACHED LIGHTING LAYOUT. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198 04.08.2021 12:58:11 UTC Mohammad Alam (QRMANR) MATERIAL RESERVED THROUGH WO 90662179
90662185 | 2021-08-29 | A081-1SB210N2 | AB_1LFN210N219L314 36W LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10385594 | 700002352082 | ABB MALAYSIA | Electrical | 73.21 | 4 | 29 | end of life | end of life- | Lamps | Replace | 20.07.2021 20:47:28 UTC Hareshkumar Chauhan (QRHCH2) Clear description of the problem. GTL-1 AB AREA 1E-3041 12M ELEVATION EAST SIDE OF EXCHANGER 1E-3041C/D, 1LFN210N219L215 36W LIGHT NOT WORKING. NEED TO CHECK <(>&<)> REPLACE THE FAULTY LAMPS. SCAFFOLDING REQUIRED 3-4 MTR. APPROX. FOR LOCATION REFER ATTACHED LIGHTING LAYOUT. PEFS: Prioriteit: Additional mitigations : X Scaffold Electrical tasks: X E-isolation X JHA needed Requester Name : HARESHKUMAR CHAUHAN Phone : 70483198 04.08.2021 12:58:48 UTC Mohammad Alam (QRMANR) MATERIAL RESERVED THROUGH WO 90662179
90662195 | 2021-07-28 | A081-1SB210N2 | poor lighting nr 1R-3027 | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10385619 | 700002352082 | ABB MALAYSIA | Electrical | 552.03 | 8.1 | 8.1 | end of life | end of life- | Lamps | Replace
90662222 | 2021-07-24 | A081-0S0123B | 0S-123 B HC FILTER REPLACEMENT. | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10385641 | 700002200643 | DKME | Integrity | 16841.03 | 46 | 47
90662223 | 2021-07-24 | A081-0S0143A | 0S-143 A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10385642 | 700002201324 | DKME | Integrity | 388.68 | 30 | 30
90662364 | 2021-07-24 | A081-0A8350 | BSRD HMI SCREEN LOGIN ISSUE | MX04 | M_X_X | Schedule Breaker | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10385582 | 700002779390 |  | Integrity | 0 | 0 | 0 | Other - please specify in text field | Other - please specify in text field-User group unauthorised. | Other - please specify in text field | Other - please specify in text field
90662486 | 2021-07-25 | A081-1A8324 | TR1 DAF SMALL WHEEL B LINING DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10385794 | 700002348718 |  | Rotating | 158.79 | 0 | 0 | Other - please specify in text field | Other - please specify in text field-wheel material defect | Rotating element | Replace
90662571 | 2021-08-18 | A081-1A8324 | DAF-1 SCRAPER & CHAIN TILTED TO BE REFIX | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10385824 | 700002348718 |  | Rotating | 5414.02 | 121 | 417 |  |  |  |  | 24.07.2021 14:04:50 UTC Jagdishkumar Patel (QRJPAA) Clear description of the problem. DAf-1 Scrapper scum board is found little tilted condition due to chain is not properly tighten, same to be tighten and align scum board. PEFS: T-4.118.864 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Skimming performance is reduced and chain can break as load in single chain. Additional mitigations : Requester Name : Ghanshyam Dobaria Phone : 44032215 25.07.2021 04:18:54 UTC Raju Sutham (QRRSU3) THIS NOTIFICATION CREATED FOR DAF-1 CHAIN AND SCUM BOARD NEED TO REINSTALL PROPERLY TO AVOID SCUM BOARD DAMAGE AND FREQUENT CHAIN DE TACHMENT
90662867 | 2021-08-03 | A081-0X0104 | 0X-0104 SCREW CONVEYOR CLEANING | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10385956 | 700002206193 |  | Electrical | 83.2 | 0 | 10 | Preventive Maintenance Work | Preventive Maintenance Work- | drive system | PM | 26.07.2021 22:21:46 UTC Sivakumar Manokaran (QRSMAA) DR.M filter screw conveyer cleaning required. 27.07.2021 04:33:05 UTC Bakthavatchalan Thenral (QRBTH0) ICC required
90662907 | 2021-07-28 | A081-1A8324 | TR-1 DAF SMALL WHEEL-B DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10385971 | 700002348718 |  | Rotating | 113.21 | 0 | 0 | Other - please specify in text field | Other - please specify in text field-bad quality wheel | Other - please specify in text field | Fix / Repair
90663006 | 2022-06-02 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Emergency | 0 |  | HYDROCARBON FILTER | CM | FGP | 10386076 | 700002200043 | DKME | Integrity | 3607.26 | 21 | 47
90663018 | 2022-06-21 | A081-0S0163B | 0S-0163B DP high | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10386075 | 700002200043 | DKME | Integrity | 3403.08 | 47 | 47
90663020 | 2022-01-10 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10386073 | 700002202402 | DKME | Integrity | 3666.43 | 47 | 47
90663021 | 2022-03-13 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10386072 | 700002202402 | DKME | Integrity | 3331.82 | 21 | 47 |  | - | Filter cartridges
90663023 | 2022-04-26 | A081-0S0143A | 0S-0143A DP HIGH | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10386071 | 700002201324 | DKME | Integrity | 3425.51 | 28 | 47
90663025 | 2022-01-22 | A081-0S0143A | 0S-0143A DP HIGH | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10386070 | 700002201324 | DKME | Integrity | 348.96 | 47 | 47
90663132 | 2021-10-28 | A081-1SB210N2 | 1R-3027 FAULTY LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10386200 | 700002352082 | ABB MALAYSIA | Electrical | 215.61 | 14 | 178 | end of life | end of life- | Lighting Fixture | Replace
90663177 | 2021-08-01 | A081-2A8324 | TR 2 DAF SCRAPPER SMALL WHEEL DAMAGE | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10386160 | 700002297332 |  | Rotating | 0 | 0 | 0 | Normal Wear | Normal Wear- | Other - please specify in text field | Replace | 28.07.2021 12:52:06 UTC Mubassar Ahmed (QRMAH5) Clear description of the problem. Train 2 DAF 2A8324 SCRAPPER SMALL WHEEL "A" OUTER RUBBER LINING DAMAGED.NEED TO REPLACE. PEFS: Prioriteit: Additional mitigations : Requester Name : MUBASSAR AHMED Phone : 44032215
90663542 | 2021-08-17 | A081-1SB220N2 | AC_Poor lighting in Finger-2 & 3 | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10386361 | 700002356603 | ABB MALAYSIA | Electrical | 3667.51 | 112 | 162 | end of life | end of life- | Lamps | Replace | 01.08.2021 00:59:05 UTC Shyam Tiwari (QRSTI4) Clear description of the problem. WHILE LAMP REPLACEMENT IN SGP-1 FINGURE 2 AND 3 UNDER W/O 90659106, FOUND MANY LIGHT 36W AND 18W NOT GLOWING. NEED TO REPLACE LAMP. PEFS: Prioriteit: Additional mitigations : Electrical tasks: X JHA needed Requester Name : SHYAM TIWARI Phone : 70482757
90663596 | 2021-07-01 | A081-1A8324 | DETACHED DAF SCRAPPER TO BE REFIXED | MX04 | M_ROT_X | Emergency | 0 |  | DAF Scraper Assembly | CM | ETP | 10386371 | 700002348718 |  | Rotating | 827.89 | 0 | 44 | Other - please specify in text field | Other - please specify in text field-U-CLAMP UNSCREWED | Other - please specify in text field | Other - please specify in text field
90663705 | 2021-08-14 | A081-294XA-50200-S | 294XA50200;EHT 2ETLPU98;288RV10011,FLT** | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10386376 | 700002607282 |  | Instrumentation | 5247.55 | 52 | 490 | Loss of Heating | Loss of Heating-capillary type thermostat failed | Heat Tracing | Hardware Replacement | 01.08.2021 06:03:06 UTC Ayaz Khan Khan (QRAMU3) Clear description of the problem. 294XA50200 ELECT TRACING CMN FAIL PEFS: Prioriteit: Additional mitigations : Requester Name : MUHAMMAD AYAZ KHAN Phone : 44032413 02.08.2021 01:19:15 UTC Marikkan Thangavel (QRMTH9) Obesrved EHT circuit 2ET-LPU-98 (288RV-10011 PIPE LINE MIQ EHT) alarm. As field Operator transfered Main to Redundant EHT circuit and try to reset not getting reset.Again electrical team Transfered from Redundant to Main circuit and reset alarm, found normal.At present Main circuit is in LIVE.For rectify EHT circuit alarm need to replace capillary type thermostat to ECM type thermostat. NOTE:- checked at field with scaffolder and confirmed as Required scaffold for 4M-L X 4M-W X 20 meter Height to access EHT circuit.attached isometric drawing. 1.isolation,2.insulation removal , 3. ECM replacement, 4.Function check ,5.Reinsulation.6.Deisolation.
90663736 | 2021-08-03 | A081-1A8324 | Tr-1 DAF small wheel-C damaged | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10386463 | 700002348718 |  | Rotating | 200.41 | 0 | 0 | Normal Wear | Normal Wear- | Rotating element | Replace | 02.08.2021 13:36:22 UTC Ghanshyam Dobariya (QRGDO1) Name Ghanshyam Phone number 44032215 What is the problem? Tr-1 DAF small inner wheel-C damaged. What work is required? (Troubleshoot/Repair/replace) replace What mitigations has been taken? NA Has a photo/sketch/document been provided? yes Is the location marked with a Maintenance tag? No Special requirements for the repair: Electrical isolation Is material required for the repair? Yes Is a specialist/vendor/manpower required? No Is special tool/equipment required? yes Specify the work location: (e.g. LQ Level 1) ETP-FO-1 Is working on height and/or scaffolding required? yes
90663892 | 2021-08-04 | A081-0S8361A | SDU A BOWL MOTOR BELTS LOOSE | MX04 | M_ROT_CENT | Schedule Breaker | 0 |  | CENTRIFUGE | CM | ETP | 10386461 | 700001729713 |  | Rotating | 708.59 | 0 | 26 | Normal Wear | Normal Wear- | Other - please specify in text field | Replace | 02.08.2021 13:22:12 UTC Bagus Prasetio (QRBPR0) Clear description of the problem. SDU A Bowl belts showing loose and showing on the Bowl speed less then absolute motor speed. To be observed tightened or replace the belts PEFS: T-4.258.845 Prioriteit: Additional mitigations : X WPS/ Work instruction needed Requester Name : Bagus Phone : 44032215
90663895 | 2021-08-21 | A081-1A8324 | Removed skimming board to be fixed | MX04 | M_ROT_X | Routine Wrk Lvl 2 | 0 |  | DAF Scraper Assembly | CM | ETP | 10386446 | 700002348718 |  | Rotating | 2572.68 | 24 | 163 | Other - please specify in text field | Other - please specify in text field-Detached from L-support | Other - please specify in text field | Fix / Repair | 02.08.2021 08:14:57 UTC Jagdishkumar Patel (QRJPAA) Clear description of the problem. Train-1 DAF, removed skimming board to be fixed back after repair. PEFS: T-4.118.864 Prioriteit: Clear description of the problem, answer the following questions : Was there a process disturbance? Share info. Additional mitigations : Requester Name : JAGDISH PATEL Phone : 44032215
90663986 | 2022-07-09 | A081-0S0123A | 0S-0123A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10386570 | 700002201322 | DKME | Integrity | 3221.68 | 38 | 47
90664348 | 2021-08-16 | A081-2A8324 | TR 2 DAF SMALL WHEEEL A DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10386841 | 700002297332 |  | Rotating | 45.57 | 86 | 86 | Normal Wear | Normal Wear- | Other - please specify in text field | Replace | 08.08.2021 01:20:17 UTC Vaghasiya Bhimjibhar (QRVBH2) Clear description of the problem. TR 2 DAF SCRAPER SMALL WHELL A DAMAGED ,RUBBER PART PEAL OFF NEED TO REPAIR. SCAFFOLDING ALREADY AVAILABLE. PEFS: T-4.118.867 Prioriteit: Additional mitigations : Electrical tasks: X E-isolation Requester Name : RAJESH Phone : 44032215
90664636 | 2022-06-16 | A081-0S0123A | 0S-0123A FILTER ELEMENT TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10386964 | 700002201322 | DKME | Integrity | 3190.64 | 47 | 47
90664653 | 2021-08-11 | A081-2A8324 | Tr-2 DAF small wheel-A damaged | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10386966 | 700002297332 |  | Rotating | 873.37 | 8 | 8 | Normal Wear | Normal Wear-small wheel rubber damaged | Rotating element | Replace
90665316 | 2021-09-06 | A081-2SB210N2 | 2R-3021 Lighting not working (CCO) | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10387464 | 700002373562 | ABB MALAYSIA | Electrical | 2220.79 | 60 | 36 | end of life | end of life- | Lamps | Replace
90665560 | 2021-10-03 | A081-1SB220N2 | 1LFN220N220L119 LIGHT FIXTURE FAULT 36W | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10387635 | 700002356603 | ABB MALAYSIA | Electrical | 757.65 | 10 | 8 | end of life | end of life- | Lighting Fixture | Replace
90666010 | 2021-10-02 | A081-1SB220N2 | AC_Poor lighting in Finger- 3 | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10387726 | 700002356603 | ABB MALAYSIA | Electrical | 1852.75 | 46 | 72.1 | end of life | end of life- | Lamps | Replace
90666021 | 2021-08-23 | A081-1A8324 | TR1 DAF PART B SMALL WHEEL RUB PEEL OFF | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10387750 | 700002348718 |  | Rotating | 0 | 0 | 8 | Other - please specify in text field | Other - please specify in text field-Material poor quality | Rotating element | Replace
90666252 | 2021-01-02 | A081-1F5111 | 1F5111,BLOOM BURNERS INSPECTION | MX04 | M_FUR_X | Routine Wrk Lvl 4 | 0 |  | SMR FURNACE | CM | LPU | 10387909 | 700002348459 | KTI | Integrity | 0 | 0 | 34 |  | - | Burner - cup throat | Replace
90666288 | 2021-08-25 | A081-1A8324 | TR1 DAF SMALL WHEEL (D) DAMAGED FO1 | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10387907 | 700002348718 |  | Rotating | 314.25 | 12 | 16 | Normal Wear | Normal Wear-small wheel damage | Rotating element | Replace
90666468 | 2021-08-26 | A081-2A8324 | Tr-2 DAF small wheel-A damaged | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10388057 | 700002297332 |  | Rotating | 266.91 | 0 | 0 | Normal Wear | Normal Wear-small wheel rubber damaged | Rotating element | Replace
90666625 | 2021-09-05 | A081-2A8324 | DAF-2 DAMAGED SAMLL WHEEEL C TO BE REPLA | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10388183 | 700002297332 |  | Rotating | 403.45 | 0 | 0 | Normal Wear | Normal Wear-small wheel rubber damaged | Rotating element | Replace
90667028 | 2021-10-13 | A081-1SB210N2 | 1LFN210N219L112 36W FIXTURE REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10388449 | 700002352082 | ABB MALAYSIA | Electrical | 290.38 | 10 | 35 | end of life | end of life- | Lighting Fixture | Replace
90667030 | 2022-11-01 | A081-0S0163B | 0S-0163B HIGH DP | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10388432 | 700002200043 | DKME | Integrity | 3190.64 | 5 | 47
90667034 | 2021-09-04 | A081-1S0241 | 1S-0241 ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10388349 | 700002354895 | JFC CORPORATION | Integrity | 1348.33 | 67 | 67
90667039 | 2022-07-02 | A081-0S0163A | 0S-0163A HIGH DP | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10388431 | 700002200042 | DKME | Integrity | 3345.7 | 25 | 47
90667041 | 2022-06-28 | A081-0S0163A | 0S-0163A HIGH DP | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10388430 | 700002200042 | DKME | Integrity | 3478.55 | 47 | 47
90667043 | 2022-10-25 | A081-0S0163A | 0S-0163A HIGH DP | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10388429 | 700002200042 | DKME | Integrity | 3240.78 | 27 | 47
90667047 | 2022-03-27 | A081-0S0143B | 0S-0143B DP high | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10388422 | 700002202402 | DKME | Integrity | 518.61 | 21 | 47
90667048 | 2022-04-12 | A081-0S0143B | 0S-0143B DP high | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10388419 | 700002202402 | DKME | Integrity | 370.75 | 47 | 47
90667049 | 2022-05-31 | A081-0S0143B | 0S-0143B DP high | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10388404 | 700002202402 | DKME | Integrity | 299.81 | 25 | 47
90667262 | 2021-09-12 | A081-2A8324 | 2AM8324 SMALL DAF WHEEL D DAMAGED | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10390439 | 700002297332 |  | Rotating | 290.83 | 86 | 86
90669079 | 2021-09-18 | A081-1S0241 | 1S-0241 FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10391390 | 700002354895 | JFC CORPORATION | Integrity | 1035.97 | 29 | 67
90669360 | 2022-02-01 | A081-0S0143A | 0S-0143A FILTER DP HIGH-PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10391517 | 700002201324 | DKME | Integrity | 245.44 | 27 | 47
90669362 | 2022-07-25 | A081-0S0123A | 0S-0123A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10391516 | 700002201322 | DKME | Integrity | 9276.85 | 47 | 48
90669409 | 2021-09-21 | A081-2A8324 | Tr-2 DAF SCRAPPER SMALL WHEEL-D DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10391549 | 700002297332 |  | Rotating | 198.4 | 6 | 0 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90669544 | 2021-09-22 | A081-1A8324 | TR1 DAF SMALL WHEEL DAMAGED TO BE REPLAC | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10391615 | 700002348718 |  | Rotating | 479.57 | 12 | 0 | Normal Wear | Normal Wear- Peel off the HDPE material | Rotating element | Replace
90670021 | 2021-10-17 | A081-2SB210N2 | 2R-3021 light not working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10391791 | 700002373562 | ABB MALAYSIA | Electrical | 157.67 | 8 | 37 | end of life | end of life- | Lighting Fixture | Replace
90670038 | 2022-02-05 | A081-0A8350 | BSTD BAY 7 MAIN DOOR WIRE DETACHED FROM | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10392000 | 700002779390 |  | Integrity | 2343.33 | 202 | 194 | Normal Wear | Normal Wear-wire rope tension loose | guards/doors | Replace
90671486 | 2021-10-07 | A081-1S0241 | 1S-0241 FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10392579 | 700002354895 | JFC CORPORATION | Integrity | 1006.06 | 67 | 67
90674186 | 2021-10-13 | A081-2A8324 | DAF 2 SCRAPPER SMALL WHEEL A DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10393133 | 700002297332 |  | Rotating | 102.86 | 6 | 0 | Normal Wear | Normal Wear- | Rotating element | Replace
90674624 | 2021-10-18 | A081-2A8324 | TR2 DAF SMALL WHEEL DAMAGED TO BE REPLAC | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10393377 | 700002297332 |  | Rotating | 205.73 | 12 | 0 | Other - please specify in text field | Other - please specify in text field-Need to see the material defect | Rotating element | Replace
90674834 | 2022-01-03 | A081-0A8350 | BSTD BAY 02 ROOF GLASS REPLA*36*(POK) | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10393474 | 700002779390 |  | Integrity | 3192.31 | 511 | 511
90674835 | 2022-01-15 | A081-0A8350 | BSTD BAY 03 ROOF GLASS REPLACE*30* QTY | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10393475 | 700002779390 |  | Integrity | 17967.26 | 348 | 348
90674836 | 2021-11-17 | A081-0A8350 | BSTD BAY 4 ROOF GLASS REPLACE*49*(POK) | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10393476 | 700002779390 |  | Integrity | 0 | 0 | 294
90674837 | 2022-01-22 | A081-0A8350 | BSTD BAY 05 ROOF GLASS REPLACE*30*QTY | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10393477 | 700002779390 |  | Integrity | 11887.42 | 610 | 610
90674838 | 2022-02-02 | A081-0A8350 | BSTD BAY 06 ROOF GLASS REPLACE*60*QTY | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10393478 | 700002779390 |  | Integrity | 13126.41 | 839 | 839
90674839 | 2022-02-23 | A081-0A8350 | BSTD BAY 07 ROOF GLASS REPLACE*60*QTY | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10393479 | 700002779390 |  | Integrity | 13632.68 | 620 | 620
90674840 | 2021-11-17 | A081-0A8350 | BSTD BAY 08 ROOF GLASS REPLACE*22*(POK) | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10393480 | 700002779390 |  | Integrity | 0 | 0 | 7
90674841 | 2022-02-26 | A081-0A8350 | BSTD BAY 09 ROOF GLASS REPLACE*30*QTY | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10393481 | 700002779390 |  | Integrity | 12147.99 | 460 | 460
90675177 | 2021-11-28 | A081-2SB200N2 | PMFLT_2LFN200N206L317 400W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10393779 | 700002373557 | ABB MALAYSIA | Electrical | 21.47 | 8 | 40 | end of life | end of life- | Lamps | Replace
90675179 | 2022-01-11 | A081-2SB200N2 | PMFL_U23100 FAULTY LAMP FINFAN PLATFORM | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10393781 | 700002373557 | ABB MALAYSIA | Electrical | 1778.51 | 24 | 61 | end of life | end of life- | Lamps | Replace
90675180 | 2022-01-05 | A081-2SB200N2 | PMFLT_U23100 36W FAULTY LAMP PIPERACK | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10393784 | 700002373557 | ABB MALAYSIA | Electrical | 384.97 | 24 | 42 | end of life | end of life- | Lamps | Replace
90675195 | 2021-10-30 | A081-2A8324 | 2A-8324 DAF SMALL WHEEL-A DAMAGED | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10393774 | 700002297332 |  | Rotating | 208.34 | 8 | 86 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90675203 | 2021-10-24 | A081-294XA-50200-S | 294XA502002ET-LPU-70,EHT,TRIPPED;RECTIFY | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10393815 | 700002607282 |  | Instrumentation | 4113.95 | 12 | 0 | Loss of Heating | Loss of Heating-Redundant EHT ECM alarm contact failed | Heat Tracing | Hardware Replacement
90675322 | 2022-01-18 | A081-2SB210N2 | BB_HPS-1_36W FAULTY LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10393838 | 700002373562 | ABB MALAYSIA | Electrical | 6506.08 | 147 | 297 | end of life | end of life- | Lamps
90675354 | 2021-12-04 | A081-2SB200N2 | PMFL_U28100 FAULTY LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10393837 | 700002373557 | ABB MALAYSIA | Electrical | 56.88 | 12 | 3 | end of life | end of life- | Lamps | Replace
90675355 | 2021-12-30 | A081-2SB200N2 | PMFL_U28500 FAULTY LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10393836 | 700002373557 | ABB MALAYSIA | Electrical | 453.92 | 24 | 24 | end of life | end of life- | Lamps | Replace
90675356 | 2021-12-07 | A081-2SB200N2 | PMFL_U23600 FAULTY LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10393835 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 0 | 6 | end of life | end of life- | Lamps | No action
90675357 | 2021-12-23 | A081-2SB200N2 | PMFL_U23200 FAULTY LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10393834 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 0 | 4 | end of life | end of life- | Lamps | No action
90675358 | 2021-12-21 | A081-2SB200N2 | PMFL_U23100 FAULTY LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10393833 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 32 | 4 | end of life | end of life- | Lamps
90675360 | 2021-12-23 | A081-2SB210N2 | BB_HPS-1_18W FAULTY LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10393825 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 0 | 32 | end of life | end of life- | Lamps | No action
90675361 | 2022-01-15 | A081-2SB210N2 | BB_HPS-1_18W FAULTY LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10393823 | 700002373562 | ABB MALAYSIA | Electrical | 828.25 | 86 | 75 | end of life | end of life- | Lamps | Replace
90675655 | 2021-11-18 | A081-1SB220N2 | POOR LIGHTING T-1 SGP FINGER 1 | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10394163 | 700002356603 | ABB MALAYSIA | Electrical | 85.32 | 12 | 12 | end of life | end of life- | Lamps | Replace
90675905 | 2021-11-27 | A081-1S0241 | 1S-0241 ELEMENT TO BE REPLACED-> | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10394262 | 700002354895 | JFC CORPORATION | Integrity | 1003.38 | 27 | 65
90676237 | 2021-11-09 | A081-0X0104 | 0X-0104 SCREW CONVEYOR CLEANING. | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10394519 | 700002206193 |  | Electrical | 0 | 6 | 10 | Preventive Maintenance Work | Preventive Maintenance Work- | drive system | Cleaned
90677277 | 2021-11-08 | A081-2A8324 | TR2 DAF SMALL WHEEL C DAMAGE | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10395002 | 700002297332 |  | Rotating | 104.17 | 0 | 0 | Other - please specify in text field | Other - please specify in text field-Damaged wheel | Other - please specify in text field | Replace
90677912 | 2021-11-21 | A081-0X0104 | 0X-0104 CONVEYOR CLEANING | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10395348 | 700002206193 |  | Electrical | 0 | 6 | 10 | Preventive Maintenance Work | Preventive Maintenance Work- | drive system | PM
90679112 | 2022-01-22 | A081-2SB200N2 | Tube Light Damage at 2R-3123 2nd level | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10396157 | 700002373557 | ABB MALAYSIA | Electrical | 31.35 | 6 | 162 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90679667 | 2021-12-27 | A081-294XA-50200-S | 294XA-50200;ELECTRICAL LEAK RELAY TRIP | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10396377 | 700002607282 |  | Instrumentation | 1119.91 | 27.1 | 21.1 | end of life | end of life- | Relay / contactor | Adjust / reset
90679872 | 2022-01-08 | A081-0S0163B | 0S-163B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10396474 | 700002200043 | DKME | Integrity | 467.6 | 46 | 47
90680511 | 2021-12-13 | A081-2A8324 | DAF-2 SMALL WHEEL-C DAMAGED (2NOS) | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10396773 | 700002297332 |  | Rotating | 208.38 | 8 | 86 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90680591 | 2021-12-19 | A081-0X0104 | 0X-0104 SCREW CONVEYOR NEEDS CLEANING | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10396846 | 700002206193 |  | Electrical | 0 | 0 | 10
90680890 | 2022-01-23 | A081-0S0143A | 0S-0143A FILTER DP HIGH > | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10397036 | 700002201324 | DKME | Integrity | 3330.04 | 0 | 47
90680900 | 2021-12-20 | A081-1F5111 | FLUE GAS SAMPLING 1F5111,MECH SUPPORT** | MX09 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10397007 | 700002348459 | KTI | Integrity | 0 | 6 | 22
90681197 | 2022-03-27 | A081-1S0241 | MTASTR S-0241 DP HIGH FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10397216 | 700002354895 | JFC CORPORATION | Integrity | 2408.28 | 0 | 53
90681924 | 2022-07-08 | A081-0S0143A | 0S-0143A FILTER DP HIGH | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10397778 | 700002201324 | DKME | Integrity | 3839.52 | 46 | 47
90682363 | 2022-02-08 | A081-FIRE HYDRANT | TF,LEAK, WAT,FIRE HYDRANT FH373;REPLACE | MX04 |  | Routine Wrk Lvl 3 | 0 |  | FIRE HYDRANT | CM | UTL | 10397948 |  |  |  | 1869.75 | 7 | 26 | Normal Wear | Normal Wear- |  | Replace
90682376 | 2021-12-27 | A081-1SB210N2 | PMFL_1SB210N2 CKT-31/32/34 NEED RCD TEST | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10397869 | 700002352082 | ABB MALAYSIA | Electrical | 0 | 10 | 18 | Software / Hardware fault | Software / Hardware fault- | Fuse / MCB | Check/ Inspect/ Test
90682987 | 2022-03-23 | A081-1SB210N2 | AB_FIN FAN TOP LIGHTING CABLE FAULTY | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10398231 | 700002352082 | ABB MALAYSIA | Electrical | 1227.02 | 52 | 64
90683027 | 2022-01-01 | A081-294XA-50200-S | 294XA50200,2ETLPU91,EHT CNTNUS ALM;V8843 | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10398227 | 700002607282 |  | Instrumentation | 1196.44 | 128 | 194 | Incorrect setting/calibration | Incorrect setting/calibration-main and redunt failure(capillary type) | Heat Tracing | Field repair
90683347 | 2022-04-03 | A081-1SB220N2 | Poor lighting, SGP train-1 U-1200 area | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10398372 | 700002356603 | ABB MALAYSIA | Electrical | 472.48 | 24 | 24 | end of life | end of life- | Lamps | Replace
90683381 | 2022-01-10 | A081-2SB200N2 | BA Exch side All Norm Light Not working | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10398424 | 700002373557 | ABB MALAYSIA | Electrical | 271.21 | 24 | 24 | end of life | end of life- | Lamps | Replace
90683528 | 2022-01-31 | A081-2SB200N2 | 2TH200E41701A/B FAULTY THERMOSTAT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10398488 | 700002373557 | ABB MALAYSIA | Electrical | 3930.01 | 34 | 48 | end of life | end of life- | Thermostat / Temp. relay | Replace
90683532 | 2022-01-15 | A081-2SB200N2 | 2LFN200N214L214 LAMP NOT WORKING 150W | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10398470 | 700002373557 | ABB MALAYSIA | Electrical | 169.11 | 10 | 50 | end of life | end of life- | Lamps | Repair / correct
90683549 | 2022-05-09 | A081-0S0163B | 0S-0163B FILTER DP HIGH | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10398455 | 700002200043 | DKME | Integrity | 398.07 | 28 | 47
90683555 | 2022-01-08 | A081-2A8324 | DAF 2 SCRAPPER SMALL WHEEL A DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10398508 | 700002297332 |  | Rotating | 183.48 | 0 | 86 | Other - please specify in text field | Other - please specify in text field-wheel material | Rotating element | Replace
90683563 | 2022-01-10 | A081-1A8324 | TR1 DAF SMALL WHEEL A RUBBR LINING DMGED | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10398497 | 700002348718 |  | Rotating | 0 | 0 | 86 | Other - please specify in text field | Other - please specify in text field-damaged small ehwwl | Other - please specify in text field | Replace
90687322 | 2022-02-14 | A081-294XA-50200-S | 294XA50200,2ETLPU59,EHT,TRIPPED;RECTIFY* | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10399693 | 700002607282 |  | Instrumentation | 4998.29 | 34 | 228.8 | Current/voltage -out of limit | Current/voltage -out of limit- | Heat Tracing | Field repair
90688403 | 2022-02-02 | A081-2SB210N2 | T2 BB_HPS-1_18W FAULTY LAMP FinFans | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10400314 | 700002373562 | ABB MALAYSIA | Electrical | 712.57 | 55 | 72
90688423 | 2022-02-07 | A081-294XA-50200-S | 294XA50200,2ETLPUHD3,EHT,TRPPD;RECTIFY** | MX04 | I_MIS_PFC | Routine Wrk Lvl 1 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10400419 | 700002607282 |  | Instrumentation | 196.09 | 15 | 47 | Incorrect setting/calibration | Incorrect setting/calibration- | Heat Tracing | Field repair
90688830 | 2022-02-05 | A081-2A8324 | 2AM8324 DAF-2 WHEEL D DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10400630 | 700002297332 |  | Rotating | 0 | 18 | 18 | Normal Wear | Normal Wear- | Rotating element | Replace
90689364 | 2022-11-05 | A081-2SB210N2 | BB_ABOVE FINFAN 18W LIGHTING FIXTURE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10400923 | 700002373562 | ABB MALAYSIA | Electrical | 4957.25 | 15 | 84 | end of life | end of life- | Lamps
90689383 | 2022-02-20 | A081-0A8350 | BSTD BAY 8 DOOR LCP COVER DAMAGED | MX04 | M_X_X | Routine Wrk Lvl 3 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP |  | 700002779390 |  | Integrity | 0 | 0 | 0
90689386 | 2022-02-12 | A081-2A8324 | DAF-2 SMALL WHEEL A DAMAGED | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10400998 | 700002297332 |  | Rotating | 294.44 | 86 | 86 | Normal Wear | Normal Wear- | Rotating element | Replace
90691131 | 2022-02-27 | A081-2A8324 | TR-2 DAF SMALL WHEEL-C DAMAGED | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10402134 | 700002297332 |  | Rotating | 388.3 | 86 | 86 | Normal Wear | Normal Wear- | Rotating element | Replace
90691232 | 2022-02-22 | A081-0A8350 | BSTD BAY 8 TRIPPED FREQUENTLY | MX04 | M_X_X | Schedule Breaker | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10402284 | 700002779390 |  | Integrity | 91.4 | 72 | 72 | Loose connection | Loose connection- | Switch / Isolator | Check/ Inspect/ Test
90691727 | 2022-03-07 | A081-0P2021 | ACC CLEANING PUMP MOTOR/ELECTRICAL FAULT | MX04 | M_PUM_RECI | Routine Wrk Lvl 1 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10402545 | 700002199414 | PRATISSOLI | Rotating | 0 | 8 | 8 | Other - please specify in text field | Other - please specify in text field-CP Emerg push button activated | Other - please specify in text field | Check/ Inspect/ Test
90692442 | 2022-03-02 | A081-0P2021 | Leak, pin hole PG imp line 0P2021 | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10402922 | 700002199414 | PRATISSOLI | Rotating | 0 | 0 | 8 | Other - please specify in text field | Other - please specify in text field-NEED TO REPALCE L-BOW | Instrumentation | Replace
90693952 | 2022-06-13 | A081-2SB210N2 | 2LFN210N209L207 Light Damage nr2E3036 | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10403040 | 700002373562 | ABB MALAYSIA | Electrical | 256.32 | 10 | 50 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90694189 | 2022-08-07 | A081-2SB210N2 | PMFLT_BB AREA LIGHT DIFFUSER DAMAGED | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10403065 | 700002373562 | ABB MALAYSIA | Electrical | 1024.48 | 8 | 8 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90694222 | 2022-08-08 | A081-2SB210N2 | PMFLT_BB AREA 18/36W FIXTURE FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10403084 | 700002373562 | ABB MALAYSIA | Electrical | 1515.24 | 10 | 32 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90694334 | 2022-08-21 | A081-2SB200N2 | BA AREA LAMPS 18W/36W/150W/250W/400W/NOT | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10403198 | 700002373557 | ABB MALAYSIA | Electrical | 9286.35 | 120 | 862.1 | end of life | end of life- | Lamps | Replace
90694494 | 2022-03-17 | A081-2SB210N2 | PMFLT_2JB7722077 JB MOUNTING LOOSE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10403315 | 700002373562 | ABB MALAYSIA | Electrical | 34.85 | 8 | 8 | Loose connection | Loose connection- | Lighting Fixture | retight
90694823 | 2022-08-07 | A081-2SB200N2 | PMFLT_2LFN200N211L311 DIFFUSER DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10403544 | 700002373557 | ABB MALAYSIA | Electrical | 252.48 | 4 | 4 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90694826 | 2022-03-22 | A081-2SB200N2 | PMFLT_2LFN200N205L312 MOUNTING BOLT LOSE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10403584 | 700002373557 | ABB MALAYSIA | Electrical | 91.82 | 10 | 10 |  | - | Lighting Fixture
90695322 | 2022-05-08 | A081-1SB210N2 | 1SB210N2-Q51 MCB TRIP - AB AREA | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10404030 | 700002352082 | ABB MALAYSIA | Electrical | 495.19 | 14 | 56 | Insulation failure | Insulation failure-400W BALLAST FAULTY | Lamps | Replace
90695361 | 2022-06-20 | A081-2SB210N2 | T2-BB area PC-16 FLOOR LAMPS NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10403956 | 700002373562 | ABB MALAYSIA | Electrical | 0 | 18 | 18 | end of life | end of life- | Lamps | Replace
90695377 | 2022-11-16 | A081-1SB210N2 | 1LFN210N214L116 - LIGHTING FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10404029 | 700002352082 | ABB MALAYSIA | Electrical | 0 | 16 | 56 | end of life | end of life- | Lighting Fixture | Replace
90696506 | 2022-04-19 | A081-2SB200N2 | PMFLT_LIGHTING MAINTN/CLEAN/RETIGHT/REPR | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10404480 | 700002373557 | ABB MALAYSIA | Electrical | 310.43 | 20 | 60 | Dust Accumulation | Dust Accumulation- | Lighting Fixture | clean
90696572 | 2022-03-26 | A081-1F5111 | 1F-5111 IR SCANNING | MX09 | M_FUR_X | Routine Wrk Lvl 1 | 0 |  | SMR FURNACE | CM | LPU | 10404710 | 700002348459 | KTI | Integrity | 192.27 | 82 | 85 | Other - please specify in text field | Other - please specify in text field-IR SCANNING AND INSPECTION | Furnace tube | Test
90696640 | 2022-04-25 | A081-2SB200N2 | PMFLT_BA AREA LIGHT & JB BOLTS LOOSE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10404655 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 4 | 4 | Corrosion | Corrosion- | Lighting Fixture | retight
90696703 | 2022-03-24 | A081-294XA-50200-S | 2SB400E10+Q14 -RECTIFY MCB TRP,243RV02 | MX04 |  | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10404794 |  |  |  | 318.26 | 43 | 98.2 | Power / other utility failure | Power / other utility failure-Redudant EHT tripping on Earth fault | Heat Tracing | Disconnect / Reconnect
90696780 | 2022-08-27 | A081-1SB210N2 | AB AREA LAMPS ARE NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10404853 | 700002352082 | ABB MALAYSIA | Electrical | 395.66 | 37 | 40 | end of life | end of life- | Lighting Fixture | Replace
90696805 | 2022-08-28 | A081-1SB210N2 | BUSTED LAMPS/DIFFUS NEED TO REPL 1K-3001 | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10404854 | 700002352082 | ABB MALAYSIA | Electrical | 1353.45 | 8 | 44 | end of life | end of life- | Lamps | Replace
90696806 | 2022-09-06 | A081-1SB210N2 | BUSTED LAMPS/DIFFUS NEED TO REPL 1K-3041 | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10404855 | 700002352082 | ABB MALAYSIA | Electrical | 0 | 0 | 64
90696807 | 2022-05-07 | A081-1SB210N2 | LIGHTING COVER DETACHED & WATER INSIDE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10404856 | 700002352082 | ABB MALAYSIA | Electrical | 70.1 | 10 | 8 | Ingress of water / condensation | Ingress of water / condensation- | Lighting Fixture | Replace
90696974 | 2022-04-10 | A081-2SB210N2 | Tubelight fitting detached from the supp | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10404996 | 700002373562 | ABB MALAYSIA | Electrical | 266.17 | 10 | 50 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90697037 | 2022-04-26 | A081-294XA-50200-S | 294XA50200,2ET-LDF-016 FLT,CABL DM | MX04 |  | Routine Wrk Lvl 4 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10404700 |  |  |  | 0 | 8.1 | 8.1 | Loss of Heating | Loss of Heating-during RV replacement found MIQ cabl dam | Heat Tracing | Disconnect / Reconnect
90700275 | 2022-04-05 | A081-0P2021 | ASU7: ALLCLEANING ASSEMBLY NOT WORKING | MX04 | M_PUM_RECI | Schedule Breaker | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10405886 | 700002199414 | PRATISSOLI | Rotating | 0 | 24 | 8 | Other - please specify in text field | Other - please specify in text field-VFD faulty | Other - please specify in text field | Replace
90700583 | 2022-04-07 | A081-2A8324 | DAF 2 SCRPPER SMALL WHEEL A DAMGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10406042 | 700002297332 |  | Rotating | 660.04 | 4 | 0 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90700700 | 2022-04-21 | A081-2SB200N2 | BA AREA EXCHANGER SIDE LAMPS NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10403786 | 700002373557 | ABB MALAYSIA | Electrical | 174.37 | 18 | 48 | end of life | end of life- | Lamps | Replace
90700868 | 2022-05-02 | A081-1SB220N2 | PMFLT_1SB220N2 FLOODLIGHT MOUNTING LOOSE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406236 | 700002356603 | ABB MALAYSIA | Electrical | 35.47 | 12 | 12 | Other - please specify in text field | Other - please specify in text field-Mounting loose | Lighting Fixture | retight
90700872 | 2022-05-23 | A081-1SB220N2 | PMFLT_1SB220N2 LIGHT DIFFUSER CLEANING | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406215 | 700002356603 | ABB MALAYSIA | Electrical | 133.32 | 8 | 8 | Dust Accumulation | Dust Accumulation- | Lamps | clean
90700873 | 2022-05-09 | A081-1SB220N2 | PMFLT_1SB220N2LGT DIFFUSER DAMAGE 36/18W | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406214 | 700002356603 | ABB MALAYSIA | Electrical | 357.25 | 12 | 4 | Mechanical damage | Mechanical damage- | Lamps | Replace
90700919 | 2022-09-20 | A081-1SB220N2 | PMFLT_1LFN220N218L203 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406221 | 700002356603 | ABB MALAYSIA | Electrical | 374.64 | 18 | 18 | Internal failure / short | Internal failure / short- | Lighting Fixture | Replace
90700920 | 2022-09-17 | A081-1SB220N2 | PMFLT_1LFN220N218L304 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406218 | 700002356603 | ABB MALAYSIA | Electrical | 348.44 | 16 | 44 | Internal failure / short | Internal failure / short- | Lighting Fixture | Replace
90700921 | 2022-08-13 | A081-1SB220N2 | PMFLT_1LFN220N225L304 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406222 | 700002356603 | ABB MALAYSIA | Electrical | 271.01 | 10 | 36 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90700922 | 2022-08-28 | A081-1SB220N2 | PMFLT_1LFN220N225L207 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406223 | 700002356603 | ABB MALAYSIA | Electrical | 311.37 | 8 | 36 | Operating at high temperature | Operating at high temperature- | Lighting Fixture | Replace
90700923 | 2022-10-31 | A081-1SB220N2 | PMFLT_1LFN220N219L306 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406224 | 700002356603 | ABB MALAYSIA | Electrical | 304.42 | 10 | 64.3 | end of life | end of life- | Lighting Fixture | Replace
90700924 | 2022-10-31 | A081-1SB220N2 | PMFLT_1LFN220N225L210 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406225 | 700002356603 | ABB MALAYSIA | Electrical | 232.29 | 10 | 64.3 | end of life | end of life- | Lighting Fixture | Replace
90700925 | 2022-09-04 | A081-1SB220N2 | PMFLT_1LFN220N220L106 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406226 | 700002356603 | ABB MALAYSIA | Electrical | 232.29 | 0 | 65
90700926 | 2022-09-04 | A081-1SB220N2 | PMFLT_1LFN220N220L107 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406228 | 700002356603 | ABB MALAYSIA | Electrical | 367.8 | 14 | 54 | Internal failure / short | Internal failure / short- | Lighting Fixture | Replace
90700927 | 2022-10-31 | A081-1SB220N2 | PMFLT_1LFN220N226L207 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406229 | 700002356603 | ABB MALAYSIA | Electrical | 232.29 | 10 | 64.3 | end of life | end of life- | Lighting Fixture | Replace
90700928 | 2022-08-31 | A081-1SB220N2 | PMFLT_1LFN220N221L305 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406232 | 700002356603 | ABB MALAYSIA | Electrical | 309.72 | 24 | 36 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90700929 | 2022-08-31 | A081-1SB220N2 | PMFLT_1LFN220N223L121 LIGHT 36W DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406234 | 700002356603 | ABB MALAYSIA | Electrical | 232.29 | 8 | 36 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90701590 | 2022-04-17 | A081-1S0241 | 1S-0241 DP HIGH FILTER ELEMENT REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10406430 | 700002354895 | JFC CORPORATION | Integrity | 397.75 | 53 | 53
90702151 | 2022-07-27 | A081-1SB220N2 | AC_PMFLT_36W LAMP DIFFUSER DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406730 | 700002356603 | ABB MALAYSIA | Electrical | 557.88 | 16 | 8 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90702152 | 2022-05-16 | A081-1SB220N2 | AC_PMFLT_1LFN220N204L301 CABLE ARM EXPOS | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406737 | 700002356603 | ABB MALAYSIA | Electrical | 145.06 | 10 | 62 | Other - please specify in text field | Other - please specify in text field-CABLE ARMOOUR EXPOSED | Cable / Terminations | Repair / correct
90702314 | 2022-07-09 | A081-1SB220N2 | AC-AREA 1R-1116 1ST ELV LAMPS NOT WORKIN | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10407659 | 700002356603 | ABB MALAYSIA | Electrical | 25.81 | 4 | 4 | end of life | end of life- | Lamps | Replace
90702317 | 2022-10-31 | A081-1SB220N2 | BC POST TREATMENT AREA LAMPS NOT WORKING | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10407660 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 12 | 14 | end of life | end of life- | Lamps
90702339 | 2022-06-21 | A081-1F5111 | 1F5111,BNR,H14,AIR REGISTER IV STUCK UP* | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10407744 | 700002348459 | KTI | Integrity | 41.69 | 0 | 9 | Product Contamination | Product Contamination- | Air register | Fix / Repair
90703020 | 2022-09-04 | A081-1SB220N2 | PMFLT_36W LIGHT DIFFUSER DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10408066 | 700002356603 | ABB MALAYSIA | Electrical | 379.45 | 10 | 10 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90703055 | 2022-09-11 | A081-2SB210N2 | LIGHTING COVER BROKEN NEAR 2V-3041 | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10405048 | 700002373562 | ABB MALAYSIA | Electrical | 299.09 | 8 | 40 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90703362 | 2022-08-31 | A081-1SB210N2 | PMFLT_LIGHT DIFFUSER & 18W FITTING DAMAG | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10408351 | 700002352082 | ABB MALAYSIA | Electrical | 495.83 | 12 | 16 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90703373 | 2022-05-02 | A081-2A8324 | TR2 DAF SCRAPPER SMALL WHEEL MINOR DAMAG | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10408274 | 700002297332 |  | Rotating | 553.96 | 86 | 86
90703483 | 2022-05-25 | A081-1SB210N2 | PMFLT_1SO210N234L205 IP COVER MISSING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10408393 | 700002352082 | ABB MALAYSIA | Electrical | 97.07 | 8 | 8 | Mechanical damage | Mechanical damage- | Switch / Isolator | Replace
90703484 | 2022-04-28 | A081-1S0241 | 1S-0241 DP HIGH | MX09 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10408207 | 700002354895 | JFC CORPORATION | Integrity | 1243.27 | 0 | 53 |  | - | Filter cartridges
90703683 | 2022-04-30 | A081-1F5111 | 1F5111,WJ1 GLASS CRACK/BROKEN;REPLACE | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10408523 | 700002348459 | KTI | Integrity | 59.21 | 9.5 | 17.5
90704419 | 2022-05-10 | A081-294XA-50200-S | 294XA50200,EHT,2ET-LPU-100,FLT;CHK | MX04 | I_MIS_PFC | Schedule Breaker | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10409002 | 700002607282 |  | Instrumentation | 3779.73 | 44 | 302.4 | Loss of Heating | Loss of Heating-Failed Capillary type thermostat | Heat Tracing | Hardware Replacement
90704473 | 2022-05-01 | A081-1S0241 | 1S0241 DP HIGH FILTER REPLACEMENT-PRD | MX09 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10409047 | 700002354895 | JFC CORPORATION | Integrity | 1181.33 | 53 | 53
90704570 | 2022-05-17 | A081-1SB220N2 | AC_1LFN220N227L206 WATER INGRESS | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10406352 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 10 | 35 | Ingress of water / condensation | Ingress of water / condensation- | Lighting Fixture | Replace
90704716 | 2022-08-30 | A081-1SB220N2 | AC_FINFAN PF & ABOVE PF LAMPS FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10409113 | 700002356603 | ABB MALAYSIA | Electrical | 143.61 | 10 | 10 | end of life | end of life- | Lamps | Replace
90704835 | 2022-07-11 | A081-0S0143B | 0S-0143B HC FILTER TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10409190 | 700002202402 | DKME | Integrity | 3557.97 | 40 | 49
90704845 | 2022-07-19 | A081-0S0143A | 0S-0143 A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10409206 | 700002201324 | DKME | Integrity | 3240.78 | 37 | 47
90704846 | 2022-11-25 | A081-0S0143A | 0S-0143 A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10409207 | 700002201324 | DKME | Integrity | 3240.78 | 48 | 48
90704847 | 2022-11-29 | A081-0S0143B | 0S-0143 B HC FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10409209 | 700002202402 | DKME | Integrity | 3534.87 | 47 | 47
90705171 | 2022-08-09 | A081-1SB210N2 | PMFLT_HPS-1 DIFFUSRE DAMAGE 36W | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10409261 | 700002352082 | ABB MALAYSIA | Electrical | 549.88 | 8 | 8 | Mechanical damage | Mechanical damage- | Lighting Fixture
90705248 | 2022-05-22 | A081-1F5111 | DROP OBJ,REINSTATE CLADDING,APH,1F5111** | MX04 | M_FUR_X | Routine Wrk Lvl 3 | 0 |  | SMR FURNACE | CM | LPU | 10409455 | 700002348459 | KTI | Integrity | 1586.9 | 0 | 175
90705453 | 2022-08-15 | A081-0P2021 | LEAK ,WAT,PACK,0P2021 | MX04 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10409491 | 700002199414 | PRATISSOLI | Rotating | 4316.78 | 100 | 104 | Other - please specify in text field | Other - please specify in text field-Passing | Other - please specify in text field | Fix / Repair
90705697 | 2022-05-14 | A081-1S0241 | 1S-0241 FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10409714 | 700002354895 | JFC CORPORATION | Integrity | 1425.61 | 27 | 53 |  | - | Filter cartridges
90705917 | 2022-05-21 | A081-1S0241 | 1S-0241 FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10409894 | 700002354895 | JFC CORPORATION | Integrity | 1395.73 | 37 | 53
90706395 | 2022-10-30 | A081-0P2021 | ASU8 ACC FAN CLEANING MTR & LIMIT SWITCH | MX04 | M_PUM_RECI | Routine Wrk Lvl 4 | 0 |  | CLEAN PUMP FOR AIRCOOLED STEAM CONDENSER | CM | ASU | 10410119 | 700002199414 | PRATISSOLI | Rotating | 71.86 | 0 | 16 | Misalignment | Misalignment- | Belt Drive | Other - please specify in text field
90706663 | 2022-06-19 | A081-294XA-50200-S | 294XA50200,2ET-LPU-99 EHT ALM,CHNG ECM** | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10410421 | 700002607282 |  | Instrumentation | 13495.57 | 44 | 133.6 | Loss of Heating | Loss of Heating-RTD sense more value | Heat Tracing | Hardware Replacement
90706872 | 2022-05-27 | A081-1S0241 | 1S-0241 FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10410595 | 700002354895 | JFC CORPORATION | Integrity | 1241.98 | 25 | 53
90707072 | 2022-08-06 | A081-1SB220N2 | Poor Illumination 1EF-1214 C & D | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10410627 | 700002356603 | ABB MALAYSIA | Electrical | 800.04 | 16 | 24 | end of life | end of life- | Lamps | Replace
90707867 | 2022-06-12 | A081-2A8324 | TR-2 DAF SMALL WHEEL A MINOR DAMAGE | MX04 | M_ROT_X | Routine Wrk Lvl 2 | 0 |  | DAF Scraper Assembly | CM | ETP | 10410933 | 700002297332 |  | Rotating | 0 | 0 | 0
90708026 | 2022-06-01 | A081-1S0241 | 1S-0241 FILTER DP is HIGH. | MX09 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10411127 | 700002354895 | JFC CORPORATION | Integrity | 1364.34 | 28 | 53
90708346 | 2022-06-20 | A081-2SB210N2 | Poor lighting, GTL Train - 2, 2R-3025 | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10411160 | 700002373562 | ABB MALAYSIA | Electrical | 986.06 | 32 | 72 | end of life | end of life- | Lamps
90708362 | 2022-11-02 | A081-0S0123A | 0S-0123A FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10410995 | 700002201322 | DKME | Integrity | 3240.78 | 47 | 47
90708487 | 2022-07-25 | A081-1SB210N2 | Lighting Issue AB Area | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10411513 | 700002352082 | ABB MALAYSIA | Electrical | 895.43 | 48 | 48 | end of life | end of life- | Lamps
90708591 | 2022-06-16 | A081-0S0163B | 0S-0163B FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10411648 | 700002200043 | DKME | Integrity | 3507.04 | 47 | 47
90708593 | 2022-11-30 | A081-0S0123B | 0S-0123B FILTER ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10411651 | 700002200643 | DKME | Integrity | 3240.78 | 47 | 47
90708876 | 2022-06-05 | A081-1S0241 | 1S-0241 FILTER DP is HIGH. | MX09 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10411782 | 700002354895 | JFC CORPORATION | Integrity | 1235.2 | 25 | 53
90708959 | 2022-08-11 | A081-2SB200N2 | BUSTAED LAMPS REPLACMENT 2C-3601 AREA | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10410347 | 700002373557 | ABB MALAYSIA | Electrical | 125.65 | 8 | 24 | end of life | end of life- | Lamps | Replace
90708980 | 2022-06-14 | A081-0X0104 | 0X-0104 SCREW CONVEYOR TO CLEANED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 1 | 0 |  | SCREW CONVEYOR | CM | FGP | 10411877 | 700002206193 |  | Electrical | 59.16 | 0 | 10
90716984 | 2022-06-13 | A081-1S0241 | 1S-0241 FILTER REPLACMENT&SAMPLE HANOVER | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10412150 | 700002354895 | JFC CORPORATION | Integrity | 1555.66 | 62 | 62
90717341 | 2022-06-13 | A081-2A8324 | Tr-2 DAF SMALLWHEEL A BADLY DAMAGED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10412395 | 700002297332 |  | Rotating | 109.01 | 0 | 0
90717698 | 2022-07-15 | A081-0S0123A | 0S-123 A HC FILTER REPLACEMENT | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10412770 | 700002201322 | DKME | Integrity | 3741.5 | 47 | 47
90718095 | 2022-07-19 | A081-2SB210N2 | 2LFN210N204L318 LIGTING FIXTURE DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL |  | 700002373562 | ABB MALAYSIA | Electrical | 0 | 0 | 0
90718137 | 2022-06-23 | A081-1S0241 | 1S-0241 FILTER REPLACEMENT> | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10412955 | 700002354895 | JFC CORPORATION | Integrity | 1216.82 | 25 | 53
90718155 | 2022-07-06 | A081-2SB210N2 | 2LFN210N204L318 LIGTING FIXTURE DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10413074 | 700002373562 | ABB MALAYSIA | Electrical | 241.2 | 10 | 28 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90718531 | 2022-09-27 | A081-2SB200N2 | 2LFN200N206L115 LAMP 250W NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10413325 | 700002373557 | ABB MALAYSIA | Electrical | 217.16 | 8 | 33 | end of life | end of life- | Lamps | Replace
90718533 | 2022-08-16 | A081-2SB210N2 | GTL2_BRM 400W LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10413328 | 700002373562 | ABB MALAYSIA | Electrical | 250.19 | 22 | 47 | end of life | end of life- | Lamps | Replace
90718631 | 2022-07-07 | A081-294XA-50200-S | MOC#108713,2ET-LPU-099,ECM MODIFY_JC | MX04 |  | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10413228 |  |  |  | 0 | 4 | 4 | Current/voltage -out of limit | Current/voltage -out of limit- | Heat Tracing | Field repair
90718632 | 2022-07-07 | A081-294XA-50200-S | MOC#108713,2ET-LPU-100,ECM MODIFY_JC | MX04 |  | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10413229 |  |  |  | 0 | 4 | 4 | Current/voltage -out of limit | Current/voltage -out of limit- | Heat Tracing | Field repair
90718641 | 2022-11-19 | A081-294XA-50200-S | MOC#108713,2ET-LDF-032,THERMSTAT ECM RPL | MX04 |  | Routine Wrk Lvl 4 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10413177 |  |  |  | 3101.46 | 38 | 199.2 | Software fault | Software fault-As per MOC#108713 | Heat Tracing | Hardware Replacement
90718643 | 2022-10-04 | A081-294XA-50200-S | MOC#108713,2ET-LDF-031,ECM MODIFY | MX04 |  | Routine Wrk Lvl 4 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10413180 |  |  |  | 58.08 | 22 | 23 | Loss of Heating | Loss of Heating-alarm contact relay connection wiring | Heat Tracing | Disconnect / Reconnect
90718645 | 2022-10-09 | A081-294XA-50200-S | MOC#108713,2ET-LDF-033,ECM MODIFY | MX04 |  | Routine Wrk Lvl 4 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10413181 |  |  |  | 200.42 | 24 | 23 | Incorrect setting/calibration | Incorrect setting/calibration-TO CHANGE ALARM LOGIC | Heat Tracing | Field repair
90718655 | 2022-06-23 | A081-1A8324 | TR1 DAF SCRPER SMALL WHEEL B DAMAGED FO1 | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10413374 | 700002348718 |  | Rotating | 508.32 | 4 | 0 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90718799 | 2022-08-08 | A081-2SB210N2 | Lighting not working BB area | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10413530 | 700002373562 | ABB MALAYSIA | Electrical | 1454.29 | 24 | 24 | end of life | end of life- | Lamps | Replace
90718806 | 2022-07-25 | A081-2SB200N2 | BA area lighting not working | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10413551 | 700002373557 | ABB MALAYSIA | Electrical | 1463.42 | 36 | 36 | end of life | end of life- | Lamps | Replace
90718863 | 2022-06-27 | A081-1A8324 | TR1 DAF SCRPER SMALL WHEEL C/D DMGD FO1 | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10413553 | 700002348718 |  | Rotating | 118.28 | 4 | 0 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90719070 | 2022-07-02 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 |  | Routine Wrk Lvl 1 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10413626 |  |  |  | 375.27 | 46 | 47
90719071 | 2022-07-23 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10413629 | 700002200643 | DKME | Integrity | 3932.44 | 47 | 47
90719090 | 2022-07-20 | A081-1A8324 | DAF-1 WHEEL NOT ROTATE PROPERLY | MX04 | M_ROT_X | Routine Wrk Lvl 3 | 0 |  | DAF Scraper Assembly | CM | ETP | 10413685 | 700002348718 |  | Rotating | 581.13 | 22 | 22 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90719251 | 2022-06-29 | A081-1S0241 | 1S0241 FILTER ELEMENT NEED TO BE REPLACE | MX09 | M_FIL_X | Schedule Breaker | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10413768 | 700002354895 | JFC CORPORATION | Integrity | 1283.07 | 0 | 53
90720058 | 2022-07-13 | A081-0A8350 | BIOSLUDGEBARRIER GATE FOUNDATION DAMAGED | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10414318 | 700002779390 |  | Integrity | 328.63 | 108 | 108 | Other - please specify in text field | Other - please specify in text field-Extreme weather & Rain fall | Other - please specify in text field | Other - please specify in text field
90720191 | 2022-07-06 | A081-0S0123B | 0S-123B DP HIGH | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10414453 | 700002200643 | DKME | Integrity | 10652.37 | 38 | 47
90720193 | 2022-07-06 | A081-0S0143B | 0S-143B DP high | MX09 | M_FIL_X | Schedule Breaker | 0 |  | HYDROCARBON FILTER | CM | FGP | 10414454 | 700002202402 | DKME | Integrity | 4285.2 | 38 | 47
90720323 | 2022-11-23 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 |  | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10414477 |  |  |  | 3487.74 | 47 | 47
90720324 | 2022-10-24 | A081-0S0123B | 0S-0123B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10414478 | 700002200643 | DKME | Integrity | 3487.75 | 27 | 47
90720326 | 2022-07-30 | A081-0S0143A | 0S-0143A FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10414479 | 700002201324 | DKME | Integrity | 3814.08 | 47 | 47
90720327 | 2022-07-24 | A081-0S0143B | 0S-0143B FILTER ELEMENT REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10414480 | 700002202402 | DKME | Integrity | 3937.01 | 47 | 47
90721346 | 2022-07-26 | A081-1SB210N2 | Light not working 1LFN210N 224L 202 | MX04 | E_SWB_D | Routine Wrk Lvl 1 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10415066 | 700002352082 | ABB MALAYSIA | Electrical | 37.55 | 2 | 27 | end of life | end of life- | Lamps | Replace
90721355 | 2022-08-13 | A081-1SB220N2 | GTL-sgp train1 finger3 lights not work | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10415095 | 700002356603 | ABB MALAYSIA | Electrical | 2110.1 | 40 | 140 | end of life | end of life- | Lamps | Replace
90721457 | 2022-07-24 | A081-1S0241 | 1S-0241 MECH SUPPORT FOR CUTTING THE FIL | MX04 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10415166 | 700002354895 | JFC CORPORATION | Integrity | 318.22 | 6 | 6
90722357 | 2022-08-10 | A081-2SB200N2 | 2R-3121 busted lights for replacement | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10415708 | 700002373557 | ABB MALAYSIA | Electrical | 94.9 | 12 | 48 | end of life | end of life- | Lamps
90722375 | 2022-08-14 | A081-1S0241 | 1S-0241 NEW K TYPE FILTER INSPECTION | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10415783 | 700002354895 | JFC CORPORATION | Integrity | 1699.59 | 44 | 53
90722605 | 2022-11-09 | A081-0A8350 | BSTD BAY03 ROOF GLASS REPLACEMENT | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10415897 | 700002779390 |  | Integrity | 5267.42 | 620 | 620
90722607 | 2022-10-02 | A081-0A8350 | BSTD BAY02 ROOF GLASS REPLACEMENT | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10415898 | 700002779390 |  | Integrity | 8581.85 | 610 | 610
90722608 | 2022-11-13 | A081-0A8350 | BSTD BAY03 ROOF GLASS REPLACE *95*QTY | MX04 | M_X_X | Routine Wrk Lvl 4 | 0 |  | BIO SLUDGE TREATMENT AND DRYING PACKAGE | CM | ETP | 10415899 | 700002779390 |  | Integrity | 6182.27 | 733 | 733 |  | -ROOF GLASS BROKEN |  | Replace
90722972 | 2022-08-31 | A081-294XA-50200-S | 294XA50200,EHT TRP ERTH LEAK,QI10101/350 | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10416018 | 700002607282 |  | Instrumentation | 84.27 | 4 | 4 | Loss of Heating | Loss of Heating-ELR relay activated | Heat Tracing | Field repair
90722977 | 2022-08-24 | A081-294XA-50200-S | 2ET-LDF-002,MAIN CKT ALM &ELR TRIP RECTY | MX04 |  | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10416129 |  |  |  | 180.38 | 23 | 23.1 | Loss of Heating | Loss of Heating-Main CKT ECM failed | Heat Tracing | Hardware Replacement
90723212 | 2022-09-26 | A081-2SB200N2 | 2LFN200N203L314 250W LAMP REPLACEMENT | MX04 | E_SWB_D | Routine Wrk LvL 5 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10416252 | 700002373557 | ABB MALAYSIA | Electrical | 159.09 | 8 | 33 | end of life | end of life- | Lighting Fixture | Replace
90723215 | 2022-09-01 | A081-2SB200N2 | 2LFN200N204L209 18W FIXTURE DAMAGE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10416255 | 700002373557 | ABB MALAYSIA | Electrical | 125.9 | 16 | 16 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90723918 | 2022-10-18 | A081-2SB210N2 | 2LFN210N223L312 150W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10416728 | 700002373562 | ABB MALAYSIA | Electrical | 80.57 | 10 | 50 | end of life | end of life- | Lamps | Replace
90723920 | 2022-09-10 | A081-2SB210N2 | 2LFN210N223L205 150W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10416730 | 700002373562 | ABB MALAYSIA | Electrical | 128.32 | 10 | 50 | end of life | end of life- | Lighting Fixture
90723921 | 2022-09-10 | A081-2SB210N2 | 2LFN210N223L307 150W LAMP FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10416732 | 700002373562 | ABB MALAYSIA | Electrical | 119.99 | 10 | 50 | end of life | end of life- | Lighting Fixture
90724328 | 2022-10-26 | A081-2SB200N2 | BA_3121 400W LAMP REPLACEMENT ACTIVITY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10416981 | 700002373557 | ABB MALAYSIA | Electrical | 303.14 | 27 | 128 | end of life | end of life- | Lighting Fixture
90725507 | 2022-09-01 | A081-1S0241 | 1S-0241 FILTER REPLACEMENT-MOC 121885 | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10417914 | 700002354895 | JFC CORPORATION | Integrity | 1412.17 | 0 | 53
90725508 | 2022-09-17 | A081-1S0241 | 1S-0241 FILTER REPLACEMENT | MX09 | M_FIL_X | Routine Wrk Lvl 3 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10417916 | 700002354895 | JFC CORPORATION | Integrity | 1175.09 | 25 | 53 |  | - | Filter cartridges
90725509 | 2022-10-02 | A081-1S0241 | 1S-0241 Elements to b replaced 10 Micron | MX09 | M_FIL_X | Routine Wrk Lvl 4 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10417915 | 700002354895 | JFC CORPORATION | Integrity | 974.24 | 27 | 53
90725629 | 2022-09-25 | A081-1SB220N2 | 1LFN220N225L207 CABLE SHORT_TROUBLESHOOT | MX04 | E_SWB_D | Routine Wrk Lvl 3 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10418051 | 700002356603 | ABB MALAYSIA | Electrical | 202.76 | 12 | 12 | Insulation failure | Insulation failure- | Lighting Fixture | Repair / correct
90725630 | 2022-09-11 | A081-2SB200N2 | BA AREA 2C-3601 LAMPS NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10417968 | 700002373557 | ABB MALAYSIA | Electrical | 548.38 | 48 | 48 | end of life | end of life- | Lamps | Replace
90725656 | 2022-08-29 | A081-0X0104 | 0x-0104 screw conveyer glass broken | MX04 | M_PAC_CON2 | Schedule Breaker | 0 |  | SCREW CONVEYOR | CM | FGP | 10418009 | 700002206193 |  | Electrical | 363.83 | 10 | 14 | Fouling | Fouling- | frame | Replace
90726331 | 2022-11-05 | A081-1SB220N2 | AC_FINFAN ABOVE PF 18 WATT LAMPS FAULTY | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10418323 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 15 | 48
90726347 | 2022-10-01 | A081-1A8324 | CHAIN SUPPORT TO BE ALIGN,TR1 DAF SCRAPR | MX04 | M_ROT_X | Routine Wrk Lvl 4 | 0 |  | DAF Scraper Assembly | CM | ETP | 10418179 | 700002348718 |  | Rotating | 0 | 0 | 0
90726647 | 2022-09-11 | A081-2A8324 | DAMAGE,SMALL WHEEL,TRAIN 2 DAF ASSEMBLY | MX04 | M_ROT_X | Routine Wrk Lvl 1 | 0 |  | DAF Scraper Assembly | CM | ETP | 10418620 | 700002297332 |  | Rotating | 0 | 8 | 8 | Other - please specify in text field | Other - please specify in text field-small wheel damage | Other - please specify in text field | Replace
90726801 | 2022-09-05 | A081-1A8324 | DAF-1 SKIMMER SUPPORT CHAIN BROKEN | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10418641 | 700002348718 |  | Rotating | 1365.69 | 48 | 48 | Normal Wear | Normal Wear- | Bolting and Gaskets | Replace
90726885 | 2022-09-19 | A081-1SB210N2 | 1LFN210N220L317 REPLACE NEW 18W FIXTURE | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10418589 | 700002352082 | ABB MALAYSIA | Electrical | 142.35 | 10 | 50 | Mechanical damage | Mechanical damage- | Lighting Fixture | Replace
90727205 | 2022-09-18 | A081-0X0104 | 0X-104 SCREW CONVEYOR TO BE CLEANED. | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10418937 | 700002206193 |  | Electrical | 73.99 | 6 | 10 | Preventive Maintenance Work | Preventive Maintenance Work- | drive system | Cleaned
90730635 | 2022-10-11 | A081-0X0104 | 0X-104 SCREW CONVEYOR TO BE CLEANED. | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10420444 | 700002206193 |  | Electrical | 0 | 6 | 10 | Preventive Maintenance Work | Preventive Maintenance Work- | drive system | Cleaned
90730676 | 2022-10-15 | A081-2SB210N2 | 22V3401 PLATFORM LIGHTS NOT WORKING (8x) | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10420436 | 700002373562 | ABB MALAYSIA | Electrical | 142.35 | 16 | 16 | end of life | end of life- | Lamps | Replace
90730823 | 2022-10-10 | A081-1SB210N2 | 1LFE210E104L218 TB FLICKERING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10420541 | 700002352082 | ABB MALAYSIA | Electrical | 79.08 | 14 | 39 | Software / Hardware fault | Software / Hardware fault- | Lighting Fixture | Replace
90732156 | 2022-10-31 | A081-2SB210N2 | PMFL_400W FLOOD LIGHT NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10421137 | 700002373562 | ABB MALAYSIA | Electrical | 27.35 | 10 | 50 | end of life | end of life- | Lamps | Replace
90732193 | 2022-10-23 | A081-2SB210N2 | PMFL_250W FLOOD LIGHT NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10421138 | 700002373562 | ABB MALAYSIA | Electrical | 299.83 | 20 | 154 | end of life | end of life- | Lamps | Replace
90732194 | 2022-10-23 | A081-2SB210N2 | PMFL_150W FLOOD LIGHT NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10421141 | 700002373562 | ABB MALAYSIA | Electrical | 84.13 | 10 | 50 | end of life | end of life- | Lighting Fixture
90732195 | 2022-10-25 | A081-2SB210N2 | PMFL_250W FLOOD LIGHT NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10421139 | 700002373562 | ABB MALAYSIA | Electrical | 175.82 | 10 | 50 | end of life | end of life- | Lamps | Replace
90732196 | 2022-10-29 | A081-2SB210N2 | PMFL_2SB210N2_18/36W LIGHT NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD-LIGHTING, SMALL POWER | CM | GTL | 10421142 | 700002373562 | ABB MALAYSIA | Electrical | 3805.99 | 48 | 72.1 | end of life | end of life- | Lamps
90732296 | 2022-10-18 | A081-0S8361A | SDU A REQUIRE INTERNAL INSPECTION | MX04 | M_ROT_CENT | Routine Wrk Lvl 2 | 0 |  | CENTRIFUGE | CM | ETP | 10421364 | 700001729713 |  | Rotating | 0 | 38 | 38
90732353 | 2022-11-01 | A081-294XA-50200-S | 294XA50200,COMMON FLT ALM,2SS400;CHECK | MX04 | I_MIS_PFC | Routine Wrk Lvl 2 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10421357 | 700002607282 |  | Instrumentation | 1369.93 | 94 | 68 | Loss of Heating | Loss of Heating-ELR relay activated | Heat Tracing | Disconnect / Reconnect
90732371 | 2022-11-07 | A081-2SB200N2 | PMFL_2LFN200N206L215 LIGHT FAULTY 150W | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10421313 | 700002373557 | ABB MALAYSIA | Electrical | 0 | 16 | 56 | end of life | end of life- | Lamps | Replace
90732372 | 2022-10-22 | A081-2SB200N2 | PMFL_BA AREA 36/18W LAMP NOT WORKING | MX04 | E_SWB_D | Routine Wrk Lvl 4 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10421329 | 700002373557 | ABB MALAYSIA | Electrical | 1555.25 | 40 | 48 | end of life | end of life- | Lamps
90732649 | 2022-10-29 | A081-1SB210N2 | Lighting not working near 1R-3026 | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10421501 | 700002352082 | ABB MALAYSIA | Electrical | 187.93 | 12 | 50 | end of life | end of life- | Lamps | Replace
90733046 | 2022-10-23 | A081-2A8324 | TR2 DAF SCRAPER RUBBER PLATE DETACHED | MX04 | M_ROT_X | Schedule Breaker | 0 |  | DAF Scraper Assembly | CM | ETP | 10421625 | 700002297332 |  | Rotating | 0 | 12 | 12 |  | - | Other - please specify in text field | Adjust / align
90733286 | 2022-10-22 | A081-1S0241 | 1S-0241 ELEMENTS TO BE REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10421831 | 700002354895 | JFC CORPORATION | Integrity | 945.54 | 25 | 53
90734557 | 2022-11-27 | A081-294XA-50200-S | 2ET-LPU-056,ALM,MAN TO REDUDENT CHANGED | MX04 | I_MIS_PFC | Routine Wrk Lvl 3 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10422265 | 700002607282 |  | Instrumentation | 226.62 | 49.2 | 91.6 | Loss of Heating | Loss of Heating-MOC#108713 implementation | Heat Tracing | Hardware Replacement
90735906 | 2022-11-30 | A081-294XA-50200-S | MOC#108713,2ET-LPU-95,MAIN CKT ALRM&MODI | MX04 | I_MIS_PFC | Routine Wrk Lvl 4 | 0 |  | ELEC TRACING CMN FAIL | CM | SUF | 10422793 | 700002607282 |  | Instrumentation | 0 | 22 | 22 | Software fault | Software fault-modify for ECM wiring as per MOC#108713 | Heat Tracing | Disconnect / Reconnect
90735940 | 2022-11-25 | A081-0S0123A | 0S-0123A FILTER REPLACEMENT REQUIRED | MX09 | M_FIL_X | Routine Wrk LvL 5 | 0 |  | HYDROCARBON FILTER | CM | FGP | 10422861 | 700002201322 | DKME | Integrity | 3488.02 | 47 | 47
90736441 | 2022-11-10 | A081-0X0104 | 0X-0104 SCREW CONVEYOR CLEANING NEED | MX04 | M_PAC_CON2 | Routine Wrk Lvl 2 | 0 |  | SCREW CONVEYOR | CM | FGP | 10423008 | 700002206193 |  | Electrical | 0 | 6 | 10 | Preventive Maintenance Work | Preventive Maintenance Work- | Casing | Cleaned
90736491 | 2022-11-09 | A081-1S0241 | 1S-0241 FILTER ELEMENT NEED TO REPLACE | MX09 | M_FIL_X | Routine Wrk Lvl 2 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10423080 | 700002354895 | JFC CORPORATION | Integrity | 945.54 | 27 | 53
90736924 | 2022-11-26 | A081-1SB220N2 | Lights not working train-1 SGP Finger-2 | MX04 | E_SWB_D | Routine Wrk Lvl 2 | 0 |  | 400V DISTRIB BOARD - LIGHTING, SMALL PWR | CM | GTL | 10423225 | 700002356603 | ABB MALAYSIA | Electrical | 0 | 18 | 24 | end of life | end of life- | Lamps
90738604 | 2022-11-26 | A081-1S0241 | 1S-0241 ELEMENTS TO REPLACED | MX09 | M_FIL_X | Routine Wrk Lvl 1 | 0 |  | LEAN SOLVENT FILTER | CM | FGP | 10424239 | 700002354895 | JFC CORPORATION | Integrity | 930.48 | 53 | 53
[16 empty] | 3597993.95 | 68833.3 | 109046.6